## cover
|  |  |  | Doc. No. |  | TM - HTC - 100 |  |  | TM - HTC - 100
Technical Guide
|  |  | Technical Material | [5 empty] | Technical Material
Heat Transfer Calculations
sheetqty
|  |  |  | Total | 17 | sheets with a cover |  |  | 15
5
4
3
2
1 | 2019. 5. 5. | Updated. |  | S. J. Lee |  | Lee | LSJ
0 | 2008. 1. 10. | 1st Issue. |  | S. J. Lee |  | Lee | LSJ
Rev. | Date | Description |  | Prepared |  | Reviewed | Approved
나 래 열 기 술
Narai Thermal Engineering Services
| Homepage | www.ntes.co.kr |  | E-mail |  | ntes@ntes.co.kr
NTES | [7 empty] | Narai Thermal Engineering Services

## TOC
| Technical Material : |  |  | Doc. No. | TM - HTC - 100
Heat Transfer Calculations |  |  |  | Date | 2019. 5. 5.
|  |  |  | Rev. | 0
|  |  |  | Sheet No. |  | 1 | of | 1
T a b l e of C o n t e n t s
|  | 1. | Introduction
|  | 2. | Conduction
|  | 3. | Forced Convection, Internal Flow
|  | 4. | Forced Convection, External Flow
|  | 5. | Condensation
|  | 6. | Boiling
|  | 7. | Natural Convection
|  | 8. | Radiation
|  | 9. | Overall Heat Transfer Coefficient
NTES | [8 empty] | Narai Thermal Engineering Services

## 1
| Technical Material : |  |  |  |  | Doc. No. | TM - HTC - 100
Heat Transfer Calculations | [5 empty] | Date | 2019. 5. 5.
[6 empty] | Revision | 0
[6 empty] | Sheet No. |  | 1 | of | 15
|  | 1. | Introduction
Heat transfer calculations are examplified using correlations which are shown in the material " Heat Transfer Fundamentals ".
To utilize the calculations, data files as below shall be opened in advance.
|  |  | " | fluidproperties | "
|  |  | " | materials ASTM | "
|  |  | " | materials common | "
|  |  | " | materials JIS | "
|  |  | " | materials KS | "
|  |  | " | materials standard design | "
Fluid Properties
Water and Steam
IAPWS Industrial Formulation 1977 are used.
Gas Mixture
TEMA, Section 8, P-7 Properties of Gas and Vapor Mixture is referred to.
NTES | [10 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## conduction
| Technical Material : | [22 empty] | Doc. No. |  | TM - HTC - 100
Heat Transfer Calculations | [23 empty] | Date |  | 2019. 5. 5.
[24 empty] | Revision |  | 0
[24 empty] | Sheet No. |  |  | 2 | of | 15
|  | 2. | Conduction
Fourier's Law is the fundamental equation for steady state and one dimensional.
|  |  |  | q | = | - | k | dT
dx
[5 empty] | Where, |  |  | q |  | Heat Flux
Heat Transfer Rate per unit area normal to direction of heat flow
[8 empty] | k |  | Thermal Conductivity
[8 empty] | T |  | Temperature
[8 empty] | x |  | Distance in direction of heat flow
Temperature Profile in Plane Wall
Calculation
Material
|  |  |  | T1 | [9 empty] | T1 | = | 150 |  |  | ℃ |  |  |  | ASTM
[14 empty] | T2 | = | 50 |  |  | ℃ |  |  |  | plate
[9 empty] | dT |  |  |  |  | k | = | #VALUE! |  |  | kcal/m.h.℃ |  |  | <- | A 516-70
[8 empty] | T2 | [5 empty] | q | = | #VALUE! |  |  | kcal/m2.h
dx
[6 empty] | 3.5 | mm | -> | 0.0035 |  | m
Cylindrical Wall in Tube
[9 empty] | ID |  | OD
[6 empty] | Ti |  | To | 43.8 |  | 50.8 |  | mm
[9 empty] | 0.0438 |  | 0.0508 |  | m
t
[10 empty] | 3.5 | mm
|  |  |  | Equation | [11 empty] | Calculation
Material
|  |  |  | q | = | - |  | 2 | k |  | dT |  |  |  |  | Ti | = | 150 |  |  | ℃ |  |  |  | ASTM
[7 empty] | OD | ln( OD / ID ) | [7 empty] | To | = | 50 |  |  | ℃ |  |  |  | tube
[16 empty] | k | = | #VALUE! |  |  | kcal/m.h.℃ |  |  | <- | A 179
[5 empty] | Where, |  |  | OD |  | Tube OD | [5 empty] | q | = | #VALUE! |  |  | kcal/m2.h
[8 empty] | ID |  | Tubd ID
[8 empty] | dT |  | = | Ti | - | To
[5 empty] | * | Wall Conductance |  |  |  |  | hw | = |  |  |  | 2 | k
[15 empty] | OD | ln( OD / ID )
[5 empty] | * | Wall Resistance |  |  |  |  | rw | = | 1 | = | OD | ln( OD / ID ) |  |  |  | = | #VALUE! |  |  | m2.h.℃/kcal
[13 empty] | hw |  |  | 2 | k
NTES | [29 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## hic
| Technical Material : | [20 empty] | Doc. No. |  |  | TM - HTC - 100
Heat Transfer Calculations | [21 empty] | Date |  |  | 2019. 5. 5.
[22 empty] | Revision |  |  | 0
[22 empty] | Sheet No. |  |  |  | 3 | of |  | 15
|  | 3. | Forced Convection, Internal Flow
Fluid defined
|  |  |  | Fluid Kind |  | Saturated
|  |  |  | Fluid in DB |  | H2O
|  |  |  | Saturation |  | No
|  |  |  | Vapor "x" |  | 0
|  |  |  | Flowrate |  | 1500 |  |  | kg/h
|  |  |  | Temperature |  | 80 |  |  | ℃ | [21 empty] | Tsat
|  |  |  | Pressure |  | 7 |  |  | kg/cm2.g | [21 empty] | #VALUE! |  | ℃
|  |  |  | Fluid State |  | #VALUE!
|  |  | Fluid Properties |  |  |  |  | Bulk |  |  |  | Wall
|  |  |  | Temperature |  | T |  | 80 |  |  | Tw | 150 |  |  |  | ℃ | [14 empty] | Density
|  |  |  | Density |  | ρ |  | #VALUE! | [7 empty] | kg/m3 | [14 empty] | *** |  | kg/Nm3
|  |  |  | Viscosity |  | μ |  | #VALUE! |  |  | μw | #VALUE! |  |  |  | kg/m.h
|  |  |  | Thermal Cond. |  | λ |  | #VALUE! | [7 empty] | kcal/m.h.℃
|  |  |  | Prandtl No. |  | Pr |  | #VALUE! | [7 empty] | ---
|  |  | Tube Data | [5 empty] | Tube OD |  |  |  | Tube Thickness |  |  |  |  | No. of Tube / Pass
[9 empty] | OD |  |  |  | t |  |  |  |  | Ntb
[9 empty] | 25.4 |  | mm |  | 2.77 |  | mm |  |  | 1
|  |  |  | Tube ID |  | ID |  | = | 19.86 |  | mm | [12 empty] | = | 0.01986 |  |  | m
|  |  |  | Flow Area |  | Afpi |  | = | π / 4 |  | x | ID | ^2 | x | Ntb | [8 empty] | = | 0.00030978 |  |  | m2
|  |  | Mass Flowrate |  |  | m |  | = | [16 empty] | 1500 |  |  | kg/h
|  |  | Vol. Flowrate |  |  | Q |  | = | m | / | ρ | [13 empty] | #VALUE! |  |  | m3/h
|  |  | Fluid Velocity |  |  | V |  | = | Q | / | Afpi |  | / | 3600 | [9 empty] | = | #VALUE! |  |  | m/sec
|  |  | Mass Velocity |  |  | G |  | = | m | / | Afpi |  | = | 1500 |  |  | / | 0.00030978 | [5 empty] | = | 4842201.8508 |  |  | kg/m2.h
|  |  | Reynolds No. |  |  | Re |  | = | G x ID / μm |  |  |  | = | 4842201.8508 |  |  | x | 0.01986 |  |  | / | #VALUE! |  | = | #VALUE! |  |  | ---
Nusselt No., Nu
|  |  |  | Turbulent Flow |  | Nu | = | c |  | x | Re |  |  | ^ | m |  | x | Pr |  | ^ | n | [9 empty] | c |  | m | n
[8 empty] | c |  | x | #VALUE! |  |  | ^ | 0.8 |  | x | #VALUE! |  | ^ | 0.4 |  |  | = | #VALUE! |  |  | --- |  |  | 0.023 |  | 0.8 | 0.4
Transient Flow
|  |  |  | Friction Factor |  | f | = | ( | 0.79 |  | x | ln ( | Re |  | ) - | 1.64 |  | ) ^ | -2
[8 empty] | ( | 0.79 |  | x | ln ( | #VALUE! |  | ) - | 1.64 |  | ) ^ | -2 |  |  |  |  | = | #VALUE! |  |  | ---
[6 empty] | Nu | = |  |  |  |  | f |  | / | 8 | x ( | Re |  | - | 1000 |  | ) x | Pr
[8 empty] | 1 + | 12.7 |  | x ( | f |  | / | 8 | ) ^ | 0.5 |  | x ( | Prm |  | ^ 2 / 3 - 1 )
[7 empty] | = |  |  |  |  | #VALUE! |  | / | 8 | x ( | #VALUE! |  | - | 1000 |  | ) x | #VALUE!
[8 empty] | 1 + | 12.7 |  | x ( | #VALUE! |  | / | 8 | ) ^ | 0.5 |  | x ( | #VALUE! |  | ^ 2 / 3 - 1 ) |  | = | #VALUE! |  |  | ---
Laminar Flow
|  |  |  | Peclet No. |  | Pe | = | Re x Pr |  |  | = | #VALUE! |  | x | #VALUE! |  | = | #VALUE! | [12 empty] | Tube Lgt
|  |  |  | Tube ID / Lgt |  | r | = | #VALUE! |  | / | #VALUE! | [5 empty] | = | #VALUE! | [12 empty] | 1000
|  |  |  | Graetz No. |  | Gz | = | Pe x r |  | = | #VALUE! |  |  | x | #VALUE! |  | = | #VALUE!
[5 empty] | Gz > 100 | Nu | = | 1.86 x Gz ^ ( 1 / 3 ) |  |  |  |  | = | 1.86 |  | x | #VALUE! |  | ^ ( 1 / 3 ) |  |  |  |  | = | #VALUE! |  |  | --- |  |  | Correction Factor
[5 empty] | Gz <= 100 | Nu | = | 3.66 |  | + |  | 0.085 |  | x | Gz | [17 empty] | Re |  | >= | 2300
[11 empty] | 1 + | 0.047 |  | x | Gz |  | ^ ( 2 / 3 ) | [15 empty] | Hot | Cold | Hot |  | Cold
[7 empty] | = | 3.66 |  | + |  | 0.085 |  | x | #VALUE! | [8 empty] | = | #VALUE! |  |  | --- |  |  | Liquid |  | 0.25 | 0.11 | 0.14 |  | 0.14
[11 empty] | 1 + | 0.047 |  | x | #VALUE! |  | ^ ( 2 / 3 ) | [13 empty] | Vapor |  | 0 | 0.5 | 0 |  | 0
[31 empty] | Saturated |  |  | Tsat | #VALUE!
|  |  | Correction Factor | [27 empty] | #VALUE! |  | Cold
|  |  |  | Liquid |  | fh | = | ( μ / μw ) ^ p |  |  |  |  | = | ( | #VALUE! |  | / | #VALUE! |  | ) ^ | #VALUE! |  |  | = | #VALUE! |  |  | --- |  |  |  |  | #VALUE! | #VALUE! | #VALUE! |  | #VALUE!
|  |  |  | Vapor |  | fh | = | ( | T |  | + | #VALUE! |  | ) ^ | p | = ( | #VALUE! |  | + | #VALUE! |  | ) ^ | #VALUE! | = | #VALUE! |  |  | --- |  |  | p | = | #VALUE!
[9 empty] | Tw |  | + | #VALUE! |  |  |  |  | #VALUE! |  | + | #VALUE!
VBA
|  |  | H. T. Coefficint |  |  | hi | = | λ / ID x Nu x fh |  |  |  |  | = | #VALUE! |  | / | 0.01986 |  | x | #VALUE! |  | x | #VALUE! | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE!
NTES | [29 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## hoc
| Technical Material : | [20 empty] | Doc. No. |  |  |  | TM - HTC - 100
Heat Transfer Calculations | [21 empty] | Date |  |  |  | 2019. 5. 5.
[22 empty] | Revision |  |  |  | 0
[22 empty] | Sheet No. |  |  |  |  | 4 | of |  | 15
|  | 4. | Forced Convection, External Flow
|  |  | A Cylinder in Cross Flow | [5 empty] | Fluid defined
[9 empty] | Fluid Kind |  |  |  | Vapor
[9 empty] | Fluid in DB |  |  |  | Dry Air | [7 empty] | Fluid Properties |  |  |  |  | Bulk
[9 empty] | Saturation |  |  |  | No | [7 empty] | Temperature |  |  |  | T | 32 |  |  | ℃ |  |  | Density |  |  | Tsat
[9 empty] | Vapor "x" |  |  |  | 0 | [7 empty] | Density |  |  |  | ρ | #VALUE! |  |  | kg/m3 |  |  | #VALUE! | kg/Nm3 |  | *** |  | ℃
[9 empty] | Velocity |  |  | V | 10 |  | m/sec | [5 empty] | Viscosity |  |  |  | μ | #VALUE! |  |  | kg/m.h
[9 empty] | Temperature |  |  |  | 32 |  | ℃ | [5 empty] | Thermal Cond. |  |  |  | λ | #VALUE! |  |  | kcal/m.h.℃
|  |  |  | V |  |  |  |  | Pressure |  |  |  | 0 |  | kg/cm2.g | [5 empty] | Prandtl No. |  |  |  | Pr | #VALUE! |  |  | --- |  |  |  |  | Zukauskas Correlation
[9 empty] | Fluid State |  |  |  | Vapor | [20 empty] | Re | [5 empty] | C |  | m |  |  | Pr | <= | 10
[6 empty] | D |  |  | Upstream Velocity |  |  |  |  | V | = | 10 |  | m/sec | [7 empty] | = | 36000 |  |  | m/h | [14 empty] | n | 0.37
[9 empty] | Cylinder Diameter |  |  |  |  | D | = | 1000 |  | mm | [7 empty] | = | 1 |  |  | m | [5 empty] | ~ | 40 |  |  | 0.75 |  | 0.4 |  |  | Pr | > | 10
[9 empty] | Reynolds No. |  |  |  |  | Re | = | ρ x V x D / μ | [9 empty] | = | #VALUE! |  |  | --- |  |  |  | 40 |  | ~ | 1000 |  |  | 0.51 |  | 0.5 |  |  | n | 0.36
[9 empty] | Nusselt No. |  |  |  |  | Nu | = | C |  | Re | ^ | m |  | Pr | ^ | n | [7 empty] | VBA |  | 1000 |  | ~ | 200000 |  |  | 0.26 |  | 0.6
[15 empty] | = | #VALUE! |  | Re | ^ | #VALUE! |  | Pr | ^ | #VALUE! |  | = | #VALUE! |  |  | --- |  | #VALUE! |  | 200000 |  | ~ |  |  |  | 0.076 |  | 0.7
Plain Tube Bank in Cross Flow
|  |  |  | In-line |  |  |  |  | Fluid defined
[7 empty] | OD |  | Fluid Kind |  |  |  | Vapor
[9 empty] | Fluid in DB |  |  |  | Dry Air
[9 empty] | Saturation |  |  |  | No |  |  |  |  | Fluid Properties |  |  |  | Bulk |  |  |  | Wall
|  |  |  | ST |  |  |  |  | Vapor "x" |  |  |  | 0 |  |  |  |  | Temperature |  |  | T | 200 |  |  | Tw | 150 |  |  | ℃
[9 empty] | Flowrate |  |  |  | 10000 |  | kg/h |  |  | Density |  |  | ρ | #VALUE! | [6 empty] | kg/m3
[9 empty] | Temperature |  |  |  | 200 |  | ℃ |  |  | Viscosity |  |  | μ | #VALUE! |  |  | μw | #VALUE! |  |  | kg/m.h |  |  | Density
[6 empty] | SL |  |  | Pressure |  |  |  | 0 |  | mmH2O |  |  | Thermal Cond. |  |  | λ | #VALUE! | [6 empty] | kcal/m.h.℃ |  |  | #VALUE! | kg/Nm3
[9 empty] | Fluid State |  |  |  | Vapor |  |  |  |  | Prandtl No. |  |  | Pr | #VALUE! | [6 empty] | ---
Tsat
|  |  |  | Staggered |  |  |  |  | Tube Bundle Data | [22 empty] | *** | ℃
[7 empty] | SD |  | Tube OD |  |  | OD | = | 25.4 |  | mm | [9 empty] | = | 0.0254 |  |  | m
[9 empty] | Pitch, Trans |  |  | ST | = | 60 |  | mm | 2.3622 |  | < ST / OD |  |  | No. of Tubes / Row |  |  |  |  | Nt |  | 10
[9 empty] | Pitch, Longi. |  |  | SL | = | 60 |  | mm | 2.3622 |  | < SL / OD |  |  | No. of Tube Rows |  |  |  |  | Nr |  | 5
[9 empty] | Tube Lemgth |  |  | Lt | = | 1000 |  | mm | [9 empty] | = | 1 |  |  | m
|  |  |  | ST | [30 empty] | Zukauskas
[35 empty] | In-line | [10 empty] | Staggered
[35 empty] | Re | [6 empty] | C |  | m |  | Re | [5 empty] | C |  | m
[6 empty] | SL | [31 empty] | ~ | 100 |  |  | 0.9 |  | 0.4 |  |  |  |  | ~ | 500 |  | 1.04 |  | 0.4
[35 empty] | 100 |  |  | ~ | 1000 |  |  | 0.52 |  | 0.5 |  | 500 |  |  | ~ | 1000 |  | 0.71 |  | 0.5
|  |  |  | Flow Width |  |  | W | = | ( | ST | - | OD | ) | x | Nt | [9 empty] | = | 0.346 |  |  | m | [5 empty] | 1000 |  |  | ~ | 200000 |  |  | 0.27 |  | 0.63 |  | 1000 |  |  | ~ | 200000 |  | 0.35 |  | 0.6
|  |  |  | Flow Area |  |  | Ap | = | W | x | Lt | [13 empty] | = | 0.346 |  |  | m2 | [5 empty] | 200000 |  |  | ~ |  |  |  | 0.033 |  | 0.8 |  | 200000 |  |  | ~ |  |  | 0.031 |  | 0.8
|  |  |  | Mass Flowrate |  |  | m | = | [17 empty] | 10000 |  |  | kg/h | [5 empty] | Taborek
|  |  |  | Vol. Flowrate |  |  | Q | = | m | / | ρ | [13 empty] | = | #VALUE! |  |  | m3/h | [5 empty] | In-line | [12 empty] | Staggered
|  |  |  | Fluid Velocity |  |  | V | = | Q | / | Ap | / | 3600 | [11 empty] | = | #VALUE! |  |  | m/sec | [5 empty] | Re |  |  |  |  | a1 |  | a3 |  | a4 |  | m |  | Re |  |  |  | a1 | a3 | a4 | m
|  |  |  | Mass Velocity |  |  | G | = | m | / | Ap |  | = | 10000 |  | / | 0.346 | [7 empty] | = | 28901.7341 |  |  | kg/m2.h | [7 empty] | ~ | 100 |  | 0.9 |  | 1.187 |  | 0.37 |  | 0.369 |  |  |  | ~ | 100 | 1.36 | 1.45 | 0.519 | 0.343
|  |  |  | Reynolds No. |  |  | Re | = | G x OD / μ |  |  |  | = | 28901.7341 |  | x | 0.0254 |  | / | #VALUE! |  |  |  |  | = | #VALUE! |  |  | --- | [5 empty] | 100 |  | ~ | 1000 |  | 0.408 | [5 empty] | 0.54 |  | 100 |  | ~ | 1000 | 0.593 |  |  | 0.523
|  |  |  | Nusselt No. |  |  | Nu | = | C |  | Re |  | ^ | m |  | Pr |  | ^ | n | [15 empty] | 1000 |  | ~ | 10000 |  | 0.107 | [5 empty] | 0.734 |  | 1000 |  | ~ | 10000 | 0.321 |  |  | 0.612
[5 empty] | Zukauskas | [26 empty] | VBA | Fd |  | 10000 |  | ~ |  |  | 0.37 | [5 empty] | 0.605 |  | 10000 |  | ~ |  | 0.321 |  |  | 0.612
[5 empty] | In-line |  |  | = | #VALUE! |  | #VALUE! |  | ^ | #VALUE! |  | #VALUE! |  | ^ | 0.36 | [5 empty] | = | #VALUE! |  |  | --- |  |  | #VALUE! | #VALUE! |  | C | = | a1 | ( | 1.33 |  | OD | ) ^ | ( | a3 | [6 empty] | )
[5 empty] | Staggered |  |  | = | #VALUE! |  | #VALUE! |  | ^ | #VALUE! |  | #VALUE! |  | ^ | 0.36 | [5 empty] | = | #VALUE! |  |  | --- |  |  | #VALUE! | #VALUE! | [7 empty] | ST |  |  | 1 | + | 0.14 |  | Re | ^ | a4
[5 empty] | Taborek | [29 empty] | C |  | a1
[5 empty] | In-line |  |  | = | #VALUE! |  | #VALUE! |  | ^ | #VALUE! |  | #VALUE! |  | ^ | 0.33333 | [5 empty] | = | #VALUE! |  |  | --- |  |  | #VALUE! | #VALUE! |  | #VALUE! |  | #VALUE!
[5 empty] | Staggered |  |  | = | #VALUE! |  | #VALUE! |  | ^ | #VALUE! |  | #VALUE! |  | ^ | 0.33333 | [5 empty] | = | #VALUE! |  |  | --- |  |  | #VALUE! | #VALUE! |  | #VALUE! |  | #VALUE!
Correction Factor
[5 empty] | Liquid |  | fh | = | ( μ / μw ) ^ p |  |  |  |  | = | ( | #VALUE! |  | / | #VALUE! |  | ) ^ | #VALUE! |  |  | = | #VALUE! |  |  | ---
[5 empty] | Vapor |  | fh | = | ( | T |  | + | #VALUE! |  | ) ^ | p | = ( | #VALUE! |  | + | #VALUE! |  | ) ^ | #VALUE! | = | #VALUE! |  |  | ---
[10 empty] | Tw |  | + | #VALUE! |  |  |  |  | #VALUE! |  | + | #VALUE!
|  |  |  | Heat Transfer Coefficient | [30 empty] | Correction Factor
[7 empty] | h | = | λ |  | / | OD |  | x | Nu |  | x | fh |  | x | Fd | [15 empty] | Re |  |  |  | >= | 2300
[5 empty] | Zukauskas | [26 empty] | VBA |  |  |  |  | Hot |  | Cold |  | Hot |  | Cold
[5 empty] | In-line |  |  | = | #VALUE! |  | / | 0.0254 |  | x | #VALUE! |  | x | #VALUE! |  | x | #VALUE! |  |  |  | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE! |  |  | Liquid |  | 0.25 |  | 0.11 |  | 0.14 |  | 0.14
[5 empty] | Staggered |  |  | = | #VALUE! |  | / | 0.0254 |  | x | #VALUE! |  | x | #VALUE! |  | x | #VALUE! |  |  |  | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE! |  |  | Vapor |  | 0 |  | 0.5 |  | 0 |  | 0
[5 empty] | Taborek | [29 empty] | Vapor |  |  |  | Tsat |  | ***
[5 empty] | In-line |  |  | = | #VALUE! |  | / | 0.0254 |  | x | #VALUE! |  | x | #VALUE! |  | x | #VALUE! |  |  |  | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE! |  |  | #VALUE! |  | Hot
[5 empty] | Staggered |  |  | = | #VALUE! |  | / | 0.0254 |  | x | #VALUE! |  | x | #VALUE! |  | x | #VALUE! |  |  |  | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE! |  |  |  |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
[35 empty] | p | = | #VALUE!
NTES | [30 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## _2
| Technical Material : | [21 empty] | Doc. No. |  |  |  | TM - HTC - 100
Heat Transfer Calculations | [22 empty] | Date |  |  |  | 2019. 5. 5.
[23 empty] | Revision |  |  |  | 0
[23 empty] | Sheet No. |  |  |  |  | 5 | of |  | 15
|  | Circular Finned Tube Bank in Cross Flow | [15 empty] | Area Calculation |  |  |  |  | * | in | m2 | [7 empty] | Area
Area per 1 m Tube, Tube Inside
[8 empty] | t | > | 2.77 | [7 empty] | ai | = | π | x | ID | / | 1000 |  |  |  | = | 0.062392 |  | m2
Area per 1 m Tube, Tube Outside, Bare
[8 empty] | ID |  | OD |  | Df | [5 empty] | ab | = | π | x | OD | / | 1000 |  |  |  | = | 0.079796 |  | m2
[8 empty] | 19.86 |  | 25.4 |  | 57.2 | [5 empty] | Area per 1 m Tube, Fin | [9 empty] | = | 1.6533 |  | m2
[18 empty] | af | = | [ π / 4 x |  |  | 2 x ( | Df | ^2 | - | OD | ^2 | )
[8 empty] | Hf | > | 15.9 | [9 empty] | + | π | x |  | Df | x |  | tf | ] x | FPM |  | / 10^6
|  |  | tf |  |  | Pf |  | FPI |  | FPM | [7 empty] | Area per 1 m Tube, Tube Outside, Unfinned Surface
|  |  | 0.45 |  | 2.54 |  |  | 10 |  | 393 | [7 empty] | ar | = | π | x | OD | x ( | 1000 |  | - | tf | x | FPM |  | ) /10^6
|  |  | Where, |  | OD |  | Tube OD | [10 empty] | Area per 1 m Tube, Tube Outside | [9 empty] | = | 0.065684 |  | m2
[5 empty] | t |  | Tube Thickness |  |  |  |  | ID |  | Tube ID |  |  |  | ao |  | = | af | + | ar |  |  |  |  | = | 1.719 |  | m2
[5 empty] | Hf |  | Fin Height |  |  |  |  | tf |  | Fin Thick |  |  |  | Ratio of Area, Outside / Inside
[5 empty] | Df |  | Fin OD |  |  |  |  | Pf |  | Fin Pitch |  |  |  | Raoi |  | = | ao | / | ai |  |  |  |  | = | 27.5512 |  | ---
[5 empty] | FPI |  | Fin Q'ty per Inch | [10 empty] | Ratio of Area, Outside, Finned / Bare
[5 empty] | FPM |  | Fin Q'ty per Meter |  |  |  |  | * | in | mm |  |  |  | Raob |  | = | ao | / | ab |  |  |  |  | = | 21.542 |  | ---
Flow Area per 1 m Tube, through Fins
[18 empty] | Apfin |  | = | ( | Df | - | OD | ) |  |  | = | 0.026176 |  | m2
|  |  | In-line | [6 empty] | Fluid defined | [9 empty] | x | ( | 1000 |  | - | tf | x | FPM |  | ) / 10^6
[10 empty] | Fluid Kind |  |  |  | Vapor
[10 empty] | Fluid in DB |  |  |  | Dry Air
[10 empty] | Saturation |  |  |  | No |  |  |  |  | Fluid Properties |  |  |  | Bulk |  |  |  | Wall
|  |  | ST | [6 empty] | Vapor "x" |  |  |  | 0 |  |  |  |  | Temperature |  |  | T | 200 |  |  | Tw | 150 |  |  | ℃
[10 empty] | Flowrate |  |  |  | 10000 |  | kg/h |  |  | Density |  |  | ρ | #VALUE! | [6 empty] | kg/m3
[10 empty] | Temperature |  |  |  | 200 |  | ℃ |  |  | Viscosity |  |  | μ | #VALUE! |  |  | μw | #VALUE! |  |  | kg/m.h |  |  | Density
[5 empty] | SL |  |  |  |  | Pressure |  |  |  | 0 |  | mmH2O |  |  | Thermal Cond. |  |  | λ | #VALUE! | [6 empty] | kcal/m.h.℃ |  |  | #VALUE! | kg/Nm3
[10 empty] | Fluid State |  |  |  | Vapor |  |  |  |  | Prandtl No. |  |  | Pr | #VALUE! | [6 empty] | ---
Tsat
|  |  | Staggered | [6 empty] | Tube Bundle Data | [22 empty] | *** | ℃
[8 empty] | SD |  | Tube OD |  |  | OD | = | 25.4 |  | mm | [9 empty] | = | 0.0254 |  |  | m
[10 empty] | Pitch, Trans |  |  | ST | = | 60 |  | mm | 2.3622 |  | < ST / OD |  |  | No. of Tubes / Row |  |  |  |  | Nt |  | 10
[10 empty] | Pitch, Longi. |  |  | SL | = | 60 |  | mm | 2.3622 |  | < SL / OD |  |  | No. of Tube Rows |  |  |  |  | Nr |  | 5
[10 empty] | Pitch, Diag. |  |  | SD | = | 67.082 |  | mm
|  |  | ST | [6 empty] | Tube Lemgth |  |  | Lt | = | 1000 |  | mm | [9 empty] | = | 1 |  |  | m
SL
|  |  | Flow Area |  |  |  |  | Ap | = | [ | Apfin |  | + ( | ST | - | Df | ) / | 1000 |  | ] | x | Lt | x | Nt |  | = | 0.28976 |  |  | m2
|  |  | Mass Flowrate |  |  |  |  | m | = | [17 empty] | 10000 |  |  | kg/h
|  |  | Vol. Flowrate |  |  |  |  | Q | = | m | / | ρ | [13 empty] | = | #VALUE! |  |  | m3/h
|  |  | Fluid Velocity |  |  |  |  | V | = | Q | / | Ap | / | 3600 | [11 empty] | = | #VALUE! |  |  | m/sec
|  |  | Mass Velocity |  |  |  |  | G | = | m | / | Ap |  | = | 10000 |  | / | 0.28976 | [7 empty] | = | 34511.1172 |  |  | kg/m2.h
|  |  | Reynolds No. |  |  |  |  | Re | = | G x OD / μ |  |  |  | = | 34511.1172 |  | x | 0.0254 |  | / | #VALUE! |  |  |  |  | = | #VALUE! |  |  | ---
|  |  | Nusselt No. |  |  |  |  | Nu | = | C |  | Re |  | ^ | m |  | Pr |  | ^ | n
|  |  |  | Briggs | [28 empty] | VBA | Fd
|  |  |  | In-line |  |  |  |  | = | 0.091867 |  | #VALUE! |  | ^ | 0.718 |  | #VALUE! |  | ^ | 0.33333 |  | [(Pf-tf)/Hf]^0.296 |  |  |  | = | #VALUE! |  |  | --- |  |  | #VALUE! | #VALUE!
|  |  |  | Staggered |  |  |  |  | = | 0.1378 |  | #VALUE! |  | ^ | 0.718 |  | #VALUE! |  | ^ | 0.33333
[16 empty] | x [ ( Pf - tf ) / Hf ]^0.296 x ( ST / SD )^0.5 | [9 empty] | = | #VALUE! |  |  | --- |  |  | #VALUE! | #VALUE!
|  |  |  | Schmidt |  |  |  | * | Condition |  |  | : | 5 | < | af | / | ab | = | 20.7188 | < | 12
|  |  |  | In-line |  |  |  |  | = | 0.3 |  | #VALUE! |  | ^ | 0.625 |  | #VALUE! |  | ^ | 0.33333 |  | (af/ab)^-0.375) |  |  |  | = | #VALUE! |  |  | --- |  |  | #VALUE! | #VALUE!
|  |  |  | Staggered |  |  |  |  | = | 0.45 |  | #VALUE! |  | ^ | 0.625 |  | #VALUE! |  | ^ | 0.33333 |  | (ao/ab)^-0.375) |  |  |  | = | #VALUE! |  |  | --- |  |  | #VALUE! | #VALUE!
Correction Factor
|  |  |  | Liquid |  |  |  | fh | = | ( μ / μw ) ^ p |  |  |  |  | = | ( | #VALUE! |  | / | #VALUE! |  | ) ^ | #VALUE! |  |  | = | #VALUE! |  |  | ---
|  |  |  | Vapor |  |  |  | fh | = | ( | T |  | + | #VALUE! |  | ) ^ | p | = ( | #VALUE! |  | + | #VALUE! |  | ) ^ | #VALUE! | = | #VALUE! |  |  | ---
[11 empty] | Tw |  | + | #VALUE! |  |  |  |  | #VALUE! |  | + | #VALUE!
|  |  | Heat Transfer Coefficient | [31 empty] | Correction Factor
[8 empty] | h | = | λ |  | / | OD |  | x | Nu |  | x | fh |  | x | Fd | [14 empty] | Re |  | >= | 2300
|  |  |  | Briggs | [28 empty] | VBA |  |  |  | Hot | Cold | Hot |  | Cold
|  |  |  | In-line |  |  |  |  | = | #VALUE! |  | / | 0.0254 |  | x | #VALUE! |  | x | #VALUE! |  | x | #VALUE! |  |  |  | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE! |  | Liquid |  | 0.25 | 0.11 | 0.14 |  | 0.14
|  |  |  | Staggered |  |  |  |  | = | #VALUE! |  | / | 0.0254 |  | x | #VALUE! |  | x | #VALUE! |  | x | #VALUE! |  |  |  | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE! |  | Vapor |  | 0 | 0.5 | 0 |  | 0
|  |  |  | Schmidt | [30 empty] | Vapor |  |  | Tsat | ***
|  |  |  | In-line |  |  |  |  | = | #VALUE! |  | / | 0.0254 |  | x | #VALUE! |  | x | #VALUE! |  | x | #VALUE! |  |  |  | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE! |  | #VALUE! |  | Hot
|  |  |  | Staggered |  |  |  |  | = | #VALUE! |  | / | 0.0254 |  | x | #VALUE! |  | x | #VALUE! |  | x | #VALUE! |  |  |  | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE! |  |  |  | #VALUE! | #VALUE! | #VALUE! |  | #VALUE!
[35 empty] | p | = | #VALUE!
NTES | [31 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## Feff
| Technical Material : | [21 empty] | Doc. No. |  |  |  | TM - HTC - 100
Heat Transfer Calculations | [22 empty] | Date |  |  |  | 2019. 5. 5.
[23 empty] | Revision |  |  |  | 0 | 1
[23 empty] | Sheet No. |  |  |  |  | 6 | of |  | 15
Fin Efficiency
|  |  | Circular Fin |  |  |  |  | * | Schmidt Empirical Solution | [7 empty] | * | McQuiston & Tree Approximate Method
VBA
|  |  |  | ηf | = | tanh ( |  | m | he | ) | = | e ^ | ( m he ) |  | - | e ^ | ( - m he ) |  |  | x | 1 |  |  |  |  | = | #VALUE! | [5 empty] | #VALUE! |  |  | High Finned
[8 empty] | m | he |  |  | e ^ | ( m he ) |  | + | e ^ | ( - m he ) |  |  |  | m | he | [13 empty] | High Freq. Welded
[5 empty] | Where, |  |  | m |  | Efficiency Parameter
[10 empty] | = | ( | 2 | ho | ) ^ | 0.5 | [10 empty] | = | #VALUE! | [5 empty] | #VALUE!
[12 empty] | tf | kf
[10 empty] | Where, |  |  | ho | = | 1 | / | ( | 1 | + | ro | ) |  |  |  |  | = | 48.7805 |  |  | kcal/m2.h.℃
ho
[13 empty] | ho |  | Heat Transfer Coefficient, Outsie | [11 empty] | 50 |  |  | kcal/m2.h.℃
[13 empty] | ro |  | Fouling Resistance, Outside | [11 empty] | 0.0005 |  |  | m2.h.℃/kcal
[13 empty] | tf |  | Fin Thickness | [5 empty] | = | 1.2 |  | mm |  | = | 0.0012 |  |  | m |  |  | C.S.
[13 empty] | kf |  | Fin Thermal Conductivity | [11 empty] | #VALUE! |  |  | kcal/m.h.℃ |  |  | at | 220 |  | ℃
[8 empty] | he |  | Effective Fin Height
[10 empty] | = | Hf | [ | 1 | + | 0.35 |  | ln( | Df | ) ] | [6 empty] | = | 0.022781 |  |  | m |  |  | #VALUE!
Dr
[10 empty] | Where, |  |  | Dr |  | Tube OD | [6 empty] | = | 50.8 |  | mm | = | 0.0508 |  |  | m
[13 empty] | Hf |  | Fin Height | [6 empty] | = | 19.05 |  | mm | = | 0.01905 |  |  | m |  |  | Df / Dr |  |  |  |  | = | 1.75
[13 empty] | Df |  | Fin OD |  | = | Dr | + | 2 | Hf | = | 88.9 |  | mm | = | 0.0889 |  |  | m |  |  | Hf | 2 ho / ( tf kf ) |  |  |  | = | #VALUE!
Surface Efficiency
VBA
[5 empty] | ηs | = | ( | ar | + | ηf | af | ) | [13 empty] | = | #VALUE! | [5 empty] | #VALUE!
ao
[6 empty] | Where, |  |  | FPI |  | No. of Fins per Inch | [15 empty] | 5 | [5 empty] | VBA
[9 empty] | ar |  | Unfinned Surface Area | [15 empty] | #VALUE! |  |  | m2/m |  |  | #VALUE!
[9 empty] | af |  | Fin Surface Area | [15 empty] | #VALUE! |  |  | m2/m |  |  | #VALUE!
[9 empty] | ao |  | Total Surface Area
[11 empty] | = | ar | + | af | [11 empty] | = | #VALUE! |  |  | m2/m |  |  | #VALUE!
[38 empty] | Hf | 2 ho / ( tf kf ) |  |  |  | 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
[33 empty] | Df / Dr |  | 1.5 |  |  | ho | [5 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[33 empty] | Df |  | 0.0762 |  |  | m | [5 empty] | 39.3701 | 78.7402 | 118.1102 | 157.4803 | 196.8504 | 236.2205 | 275.5906 | 314.9606
[33 empty] | Hf |  | 0.0127 |  |  | m he | [5 empty] | 0.57096 | 1.1419 | 1.7129 | 2.2838 | 2.8548 | 3.4257 | 3.9967 | 4.5677
[33 empty] | he |  | 0.014502 |  |  | ηf |  |  |  |  | 1 | 0.90385 | 0.71376 | 0.54703 | 0.42886 | 0.34798 | 0.29129 | 0.25004 | 0.21888
[38 empty] | Hf | 2 ho / ( tf kf ) |  |  |  | 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
[33 empty] | Df / Dr |  | 2 |  |  | ho | [5 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[33 empty] | Df |  | 0.1016 |  |  | m | [5 empty] | 19.685 | 39.3701 | 59.0551 | 78.7402 | 98.4252 | 118.1102 | 137.7953 | 157.4803
[33 empty] | Hf |  | 0.0254 |  |  | m he | [5 empty] | 0.6213 | 1.2426 | 1.8639 | 2.4852 | 3.1065 | 3.7278 | 4.3491 | 4.9704
[33 empty] | he |  | 0.031562 |  |  | ηf |  |  |  |  | 1 | 0.88851 | 0.68099 | 0.51131 | 0.39683 | 0.32062 | 0.26794 | 0.22986 | 0.20117
[38 empty] | Hf | 2 ho / ( tf kf ) |  |  |  | 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
[33 empty] | Df / Dr |  | 3 |  |  | ho | [5 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[33 empty] | Df |  | 0.1524 |  |  | m | [5 empty] | 9.8425 | 19.685 | 29.5276 | 39.3701 | 49.2126 | 59.0551 | 68.8976 | 78.7402
[33 empty] | Hf |  | 0.0508 |  |  | m he | [5 empty] | 0.69226 | 1.3845 | 2.0768 | 2.769 | 3.4613 | 4.1535 | 4.8458 | 5.5381
[33 empty] | he |  | 0.070333 |  |  | ηf |  |  |  |  | 1 | 0.86591 | 0.63702 | 0.46662 | 0.35831 | 0.28834 | 0.24064 | 0.20634 | 0.18056
[33 empty] | Y |  | 1 | 0.90385 | 0.71376 | 0.54703 | 0.42886 | 0.34798 | 0.29129 | 0.25004 | 0.21888
[33 empty] | X |  | 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
[33 empty] | Y |  | 1 | 0.88851 | 0.68099 | 0.51131 | 0.39683 | 0.32062 | 0.26794 | 0.22986 | 0.20117
[33 empty] | X |  | 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
[33 empty] | Y |  | 1 | 0.86591 | 0.63702 | 0.46662 | 0.35831 | 0.28834 | 0.24064 | 0.20634 | 0.18056
[33 empty] | X |  | 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
NTES | [31 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## hcd
| Technical Material : | [22 empty] | Doc. No. |  |  |  | TM - HTC - 100
Heat Transfer Calculations | [23 empty] | Date |  |  |  | 2019. 5. 5.
[24 empty] | Revision |  |  |  | 0 | 1
[24 empty] | Sheet No. |  |  |  |  | 7 | of |  | 15
|  | 5. | Condensation
Tube Inside
|  |  |  | hcd |  | = | 0.815 |  | [ | kf^3 ρf ( ρf - ρv ) g λ | [6 empty] | ] | 0.25 | [7 empty] | = | #VALUE! |  |  | kcal/m2.h.℃
π μf ID ( Ts - Tw )
[6 empty] | Where, |  |  | kf |  | Thermal Condutivity of Liquid at Film Temp. | [14 empty] | = | #VALUE! |  |  | kcal/m.h.℃
[9 empty] | ρf |  | Density of Liquid at Film Temp. | [14 empty] | = | #VALUE! |  |  | kg/m3
[9 empty] | ρv |  | Density of Vapor | [14 empty] | = | #VALUE! |  |  | kg/m3
[9 empty] | g |  | Gravitational Acceleration Velocity | [8 empty] | = | 9.8066 |  |  | m/s2 |  | = | 127094184 |  |  | m/h2
[9 empty] | λ |  | Latent Heat | [15 empty] | #VALUE! |  |  | kcal/kg
[9 empty] | μf |  | Viscosity of Liquid at Film Temp. | [14 empty] | = | #VALUE! |  |  | kg/mh
[9 empty] | ID |  | Tube ID | [14 empty] | = | 0.01986 |  |  | m
[9 empty] | Ts |  | Sat. Temp. | [14 empty] | = | #VALUE! |  |  | ℃
[9 empty] | Tw |  | Wall Temp. | [14 empty] | = | #VALUE! |  |  | ℃
[9 empty] | Tf |  | Film Temp. |  |  | = | ( Ts + Tw ) / 2 | [10 empty] | = | #VALUE! |  |  | ℃
[25 empty] | Sat. Press. at Tf | -> | #VALUE! |  |  | kg/cm2.g
|  |  | Tube |  |  |  | Horizontal
|  |  |  | hcd |  | = | 1.51 |  | Re^( -1/3 ) |  |  | Pf^( -1/3 ) | [13 empty] | = | #VALUE! |  |  | kcal/m2.h.℃
[6 empty] | Where, |  |  | Re |  | Reynolds No. |  |  |  | = | 4 x CL / μf | [9 empty] | = | #VALUE!
[9 empty] | W |  | Steam Amount condensed | [13 empty] | W | = | 10 |  |  | kg/h
[9 empty] | Γ |  | Condensing Load |  |  |  |  | = W / L | [8 empty] | Γ | = | 10 |  |  | kg/m.h
[9 empty] | L |  | Characteristic Length | [5 empty] | L |  | for | Plate |  |  |  |  | L | = | 1000 |  |  | mm
[17 empty] | π d |  | for | Vertical Tube
[17 empty] | L |  | for | Horizontal Tube
[9 empty] | Pf |  | Property Factor |  |  |  | = | μf^2 / ( kf^3 x ρf^2 x g ) | [9 empty] | = | #VALUE!
Horizontal Plate, Facing Down
|  |  |  | Parameter |  |  |  | St | = | σf |  |  |  | = |  |  | #VALUE! | [9 empty] | = | #VALUE!
[10 empty] | ( ρf - ρv ) x g |  |  |  |  | ( | #VALUE! |  | - | #VALUE! |  | ) x | g
[9 empty] | Where, |  |  | σf |  | Surface Tension of Liquid at Film Temp. | [12 empty] | = | #VALUE! |  |  | kg/m
|  |  |  | Rayleigh No. |  |  |  | Ra | = | ρf x ( ρf - ρv ) x g x ( hv - hl ) | [8 empty] | x | St^(3/2) | [6 empty] | = | #VALUE!
μf x ( Ts - Tw ) x kf
[9 empty] | = | #VALUE! |  | x ( | #VALUE! |  | - | #VALUE! |  | ) x | g | x ( | #VALUE! |  | - | #VALUE! |  | ) | x | #VALUE! |  |  | ^(3/2)
[14 empty] | #VALUE! |  | x ( | #VALUE! |  | - | #VALUE! |  | ) x | #VALUE!
[9 empty] | Where, |  |  | hv |  | Enthalpy of Sat. Vapor | [12 empty] | = | #VALUE! |  |  | kcal/kg
[12 empty] | hl |  | Enthalpy of Sat. Liquid | [12 empty] | = | #VALUE! |  |  | kcal/kg
|  |  |  | Nusselt No. |  |  |  | Nu | = | a x Ra ^ m |  |  |  | = | #VALUE! |  |  | x | #VALUE! |  |  | ^ | #VALUE! |  |  |  | = | #VALUE!
|  |  |  | hcd |  | = | kf x Nu / St^(1/2) |  |  |  |  | = | #VALUE! |  | x | #VALUE! |  | / | #VALUE! |  |  | ^(1/2) |  |  |  |  | = | #VALUE! |  |  | kcal/m2.h.℃
Horizontal Plate, Facing Up
|  |  |  | hcd |  | = | C x | kf | [ | L^3 x ρf^2 x g x ( hv - hl ) | [7 empty] | ]^(1/5) | [8 empty] | = | #VALUE! |  |  | kcal/m2.h.℃
[8 empty] | L |  | μf x ( Ts - Tw ) x kf
[6 empty] | = | 0.82 |  | #VALUE! |  | x [ | 0.08325 |  | ^3 | x | #VALUE! |  | ^2 | x | g | x ( | #VALUE! |  | - | #VALUE! |  | ) | ]^(1/5)
[9 empty] | 0.08325 |  |  |  |  | #VALUE! |  | x | ( | #VALUE! |  | - | #VALUE! |  | ) x | #VALUE!
[6 empty] | Where, |  |  | L |  | Characteristic Length | [5 empty] | = A / P = D / 4 | [7 empty] | Diameter | D | = | 333 |  |  | mm
[26 empty] | L | = | 83.25 |  |  | mm
VBA Application
|  |  | Fluid | [6 empty] | Cases
|  |  | Kind |  | Saturated |  |  |  |  | Tube |  |  | Tube |  |  | Tube |  |  | Plate |  |  | Plate |  |  | Plate
|  |  | Name |  | H2O |  |  |  |  | Inside |  |  | Outside |  |  | Outside
|  |  | Press |  | 7 |  | kg/cm2.g | [5 empty] | Horizontal |  |  | Vertical |  |  | Vertical |  |  | Horizontal |  |  | Horizontal
|  |  | Ts |  | #VALUE! |  | ℃ |  |  | OD | 25.4 |  | Lgt | 1000 |  | Tube OD |  |  | Lgt | 1000 |  | Facing Down |  |  | Facing Up
|  |  | Tw |  | 160 |  | ℃ |  |  | t | 2.77 |  |  |  |  | Q'ty | 1
|  |  | H. T. Coefficient | [6 empty] | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE!
NTES | [32 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## .2
| Technical Material : | [21 empty] | Doc. No. |  | TM - HTC - 100
Heat Transfer Calculations | [22 empty] | Date |  | 2019. 5. 5.
[23 empty] | Revision |  | 0 | 1
[23 empty] | Sheet No. |  |  | 8 | of |  | 15
Tube Bank
Fluid defined
|  |  |  | Fluid Kind |  |  |  | Saturated | [5 empty] | Tsat. |  |  |  | #VALUE! |  | ℃
|  |  |  | Fluid in DB |  |  |  | H2O | [5 empty] | Twall |  |  |  | 160 |  | ℃
|  |  |  | Saturation |  |  |  | Yes | [5 empty] | Density |  |  |  | #VALUE! |  | kg/m3
|  |  |  | Vapor "x" |  |  |  | 1
|  |  |  | Flowrate |  |  |  | 1000 |  | kg/h |  |  |  | Mass Flow |  |  | W | 1000 |  | kg/h
|  |  |  | Pressure |  |  |  | 7 |  | kg/cm2.g
|  |  |  | Fluid State |  |  |  | Sat. Vapor
Property Data
|  |  |  | Sat. Temp. | [9 empty] | Ts | [7 empty] | #VALUE! |  | ℃
|  |  |  | Wall Temp. | [9 empty] | Tw | [7 empty] | 160 |  | ℃
|  |  |  | Film Temp. |  |  | = | ( Ts + Tw ) / 2 | [5 empty] | Tf | [7 empty] | #VALUE! |  | ℃
[20 empty] | Sat. Press. at Tf | -> | #VALUE! |  | kg/cm2.g
|  |  |  | Viscosity of Liquid at Film Temp. | [9 empty] | μf | [7 empty] | #VALUE! |  | kg/mh | = | #VALUE! |  | cP
|  |  |  | Thermal Condutivity of Liquid at Film Temp. | [9 empty] | kf | [7 empty] | #VALUE! |  | kcal/m.h.℃
|  |  |  | Density of Liquid at Film Temp. | [9 empty] | ρf | [7 empty] | #VALUE! |  | kg/m3
|  |  |  | Gravitational Acceleration Velocity | [9 empty] | g | = | 9.8066 |  |  | m/s2 |  | = | 127094184 |  | m/h2
Tube Bank Data
|  |  |  | Tube OD |  |  |  | OD |  | 25.4 |  | mm | = | 0.0254 |  | m
|  |  |  | Tube Length |  |  |  | Le |  | 1000 |  | mm | = | 1 |  | m
|  |  |  | Tube Q'ty |  |  |  | Nt |  | 100 |  | ea
Vertical Tubes
Condensing Load
[5 empty] | Γ | = | W |  |  |  | = |  | 1000 | [11 empty] | = | 125.3189 |  | kg/h.m
[7 empty] | π | OD | Nt |  |  | π | 0.0254 |  | 100
Reynolds No.
[5 empty] | Re | = | 4 | Γ |  |  | = | 4 | 125.3189 | [11 empty] | = | #VALUE!
[7 empty] | μf |  |  |  |  | #VALUE!
|  |  |  | Heat Transfer Coefficient | [26 empty] | VBA
|  |  |  | h | = | 1.47 |  | Re^(-1/3) |  | [ | μf^2 |  |  | ]^(-1/3) | [10 empty] | = | #VALUE! |  | kcal/m2.h.℃ |  |  | #VALUE!
kf^3 ρf^2 g
Horizontal Tubes
[31 empty] | Equivalent Tube Q'ty | [5 empty] | Tube Pattern
|  |  |  | Equivalent Tube Q'ty | [26 empty] | 2.08 | Nt | ^ | 0.495 |  | for | Triangular
[5 empty] | ns |  | = | c |  | x | Nt |  | ^ | m |  |  |  |  | Tube Pattern | [11 empty] | 1.022 | Nt | ^ | 0.519 |  | for | Rotated Triangular
[7 empty] | = | 2.08 |  |  | 100 |  |  | 0.495 |  |  | for |  | Triangular | [5 empty] | = | 20.3265 |  |  |  |  | 1.288 | Nt | ^ | 0.48 |  | for | Square
|  |  |  | Condensing Load | [26 empty] | 1.37 | Nt | ^ | 0.518 |  | for | Rotated Square
[5 empty] | Γ | = | W |  |  |  | = |  | 1000 | [11 empty] | = | 49.1968 |  | kg/h.m
[7 empty] | Le | ns |  |  |  | 1 |  | 20.3265
Reynolds No.
[5 empty] | Re | = | 4 | Γ |  |  | = | 4 | 49.1968 | [11 empty] | = | #VALUE!
[7 empty] | μf |  |  |  |  | #VALUE! | [26 empty] | N | = | Nt | ^ | 0.5 | / | 2 | = | 5
|  |  |  | Heat Transfer Coefficient | [31 empty] | CF | = | 1 | N | ^ | -0.16667
|  |  |  | h | = | 1.51 |  | Re^(-1/3) |  | [ | μf^2 |  |  | ]^(-1/3) | [10 empty] | = | #VALUE! |  | kcal/m2.h.℃ |  |  | #VALUE! | = | #VALUE! |  | x | 0.76472
kf^3 ρf^2 g
NTES | [29 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## hboil
| Technical Material : | [22 empty] | Doc. No. |  |  |  | TM - HTC - 100
Heat Transfer Calculations | [23 empty] | Date |  |  |  | 2019. 5. 5.
[24 empty] | Revision |  |  |  | 0 | 1
[24 empty] | Sheet No. |  |  |  |  | 9 | of |  | 15
|  | 6. | Boiling
Pool Boiling
Fluid defined
[5 empty] | Fluid Kind |  |  |  | Saturated | [5 empty] | Tsat. |  |  |  | #VALUE! |  | ℃
[5 empty] | Fluid in DB |  |  |  | H2O | [5 empty] | Twall |  |  |  | 175 |  | ℃
[5 empty] | Saturation |  |  |  | Yes | [5 empty] | ΔT |  |  |  | #VALUE! |  | ℃
[5 empty] | Vapor "x" |  |  |  | 0 | [5 empty] | Critical Pressure
[5 empty] | Pressure |  |  |  | 7 |  | kg/cm2.g |  |  |  | Pc |  |  |  | #VALUE! |  | kg/cm2.g
[5 empty] | Fluid State |  |  |  | Sat. Liquid
|  |  |  | Property Data | [29 empty] | VBA
[5 empty] | Sat. Pressure |  |  |  | at | Twall | [12 empty] | #VALUE! |  |  | kg/cm2.g | [7 empty] | #VALUE!
[5 empty] | Pressure Difference | [9 empty] | ΔP | = | #VALUE! |  |  | #VALUE! |  | = | #VALUE! |  |  | kg/m2
[5 empty] | Latent Heat | [9 empty] | λ | [7 empty] | #VALUE! |  |  | kcal/kg
[5 empty] | Gravitational Acceleration Velocity | [9 empty] | g | = | 9.8066 |  |  | m/s2 |  | = | 127094184 |  |  | m/h2 |  | = | gc
Liquid Properties
[6 empty] | Density | [8 empty] | ρl | [7 empty] | #VALUE! |  |  | kg/m3
[6 empty] | Specific Heat | [8 empty] | Cl | [7 empty] | #VALUE! |  |  | kcal/kg.℃
[6 empty] | Viscosity | [8 empty] | μl | [7 empty] | #VALUE! |  |  | kg/mh |  | = | #VALUE! |  | cP
[6 empty] | Thermal Condutivity | [8 empty] | kl | [7 empty] | #VALUE! |  |  | kcal/m.h.℃
[6 empty] | Prandtl No. | [8 empty] | Prl | [7 empty] | #VALUE! |  |  | ---
[6 empty] | Surface tension | [8 empty] | σl | [7 empty] | #VALUE! |  |  | kg/m
Vapor Properties
[6 empty] | Density | [8 empty] | ρv | [7 empty] | #VALUE! |  |  | kg/m3
Nucleate Boiling
Foster and Zuber Correlation
Dimensional Form
[6 empty] | hb | = | 0.00122 |  | ( | kl ^ | 0.79 |  | Cl ^ | 0.45 |  | ρl ^ | 0.49 |  | g ^ | 0.25 |  | ) | ΔT | ^ | 0.24 |  | ΔP | ^ | 0.75
[11 empty] | σl ^ | 0.5 |  | μl ^ | 0.29 |  | λ ^ | 0.24 |  | ρv ^ | 0.24
[27 empty] | = | #VALUE! |  |  | kcal/m2.h.℃
[6 empty] | Dimensionless Form | [27 empty] | VBA
[6 empty] | Jakob No. |  |  |  | Ja | = | Cl | ΔT |  | = | #VALUE! | [17 empty] | #VALUE!
λ
[6 empty] | Bond No. |  |  |  | Bo | = | g | ρl |  | = | #VALUE! | [17 empty] | #VALUE!
σl
[6 empty] | hb | = | 0.00122 | [6 empty] | kl | [6 empty] | prl | ^ | 0.21 | Ja | ^ | 0.24 | Bo | ^ | 0.5 | ΔP | ^ | 0.75
[10 empty] | ρl ^ | 0.01 |  | ρv ^ | 0.24 |  | g ^ | 0.25 |  | μl ^ | 0.5 | [13 empty] | VBA
[27 empty] | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE!
[6 empty] | Heat Flux |  |  |  | q | = | hb | x | ΔT | [12 empty] | = | #VALUE! |  |  | kcal/m2.h
Mostinski Equation
VBA
[6 empty] | hb | = | Z1 | ( | ΔT | ) ^ | 2.33 |  |  | = | #VALUE! |  | ( | #VALUE! |  | ) ^ | 2.33 |  |  |  |  | = | #VALUE! |  |  | kcal/m2.h |  |  | #VALUE!
Where,
[7 empty] | Z1 | = | [ | 0.1 | Pc | ^ | 0.69 | ( | 1.8 | R | ^ | 0.17 | + | 4 | R | ^ | 1.2 | + | 10 | R | ^ | 10 | ) | ] ^ | 3.33
[8 empty] | Where, |  |  | Pc |  | Critical Pressure |  |  |  |  | = | #VALUE! |  |  | kg/cm2.a
[11 empty] | R |  | Reduced Pressure |  |  |  |  | = | P | / | Pc |  | = | #VALUE!
[5 empty] | Tube Bundle Effect | [5 empty] | * | Taborek |  |  |  | h | = | Fb | x | hb
Correction Factor
[6 empty] | Fb | = | 1 | + | 0.1 |  | [ |  |  | 0.785 |  | Db |  |  |  | - | 1 | ] |  |  |  |  | = | 1.6972
[13 empty] | C1 | ( | pt | / | OD | ) ^ | 2 | OD |  |  |  | Tube Pattern | [9 empty] | C1 |  | Tube Pattern
[7 empty] | Where, |  |  | C1 |  | Constant |  |  |  |  | = | 0.866 |  |  |  | for |  | Triangular | [9 empty] | 0.866 | for | Triangular
[10 empty] | OD |  | Tube OD |  |  |  |  | = | 50.8 |  | mm | [13 empty] | 0.866 | for | Rotated Triangular
[10 empty] | pt |  | Tube Pitch |  |  |  |  | = | 76 |  | mm | [13 empty] | 1 | for | Square
[10 empty] | Db |  | Bundle Diameter |  |  |  |  | = | 1000 |  | mm | [13 empty] | 1 | for | Rotated Square
NTES | [32 empty] | Narai Thermal Engineering Services
CHF ( Critical Heat Flux )
Zuber Correlation
[5 empty] | qmax |  | = | π | λ | ρv | [ | σ | g | gc | ( | ρl | - | ρv | ) | ] ^ | 0.25 |  | ( | ρl | + | ρv | ) ^ | 0.5
[8 empty] | 24 | [5 empty] | ρv | ^ | 2 | [8 empty] | ρl | [8 empty] | VBA
[27 empty] | = | #VALUE! |  |  | kcal/m2.h |  |  | #VALUE!
Minimum Heat Flux
Zuber Correlation
[5 empty] | qmin |  | = | π ^ | 2 | ( | 4 | ) ^ | 0.25 |  | λ | ρv | [ | σ | g | gc | ( | ρl | - | ρv | ) | ] ^ | 0.25
[8 empty] | 60 |  |  | 3 | [7 empty] | ( | ρl | + | ρv | ) ^ | 2 | [9 empty] | VBA
[27 empty] | = | #VALUE! |  |  | kcal/m2.h |  |  | #VALUE!
Note on AJ4: Cell is filled !
1

## -2
| Technical Material : | [21 empty] | Doc. No. |  |  |  | TM - HTC - 100
Heat Transfer Calculations | [22 empty] | Date |  |  |  | 2019. 5. 5.
[23 empty] | Revision |  |  |  | 0 | 1
[23 empty] | Sheet No. |  |  |  |  | 10 | of |  | 15
Forced Convection Boiling
Fluid defined
|  |  |  | Fluid Kind |  |  |  | Saturated | [5 empty] | Tsat. |  |  |  | #VALUE! |  | ℃
|  |  |  | Fluid in DB |  |  |  | H2O | [5 empty] | Twall |  |  |  | 175 |  | ℃ |  |  | Vapor "x"
|  |  |  | Saturation |  |  |  | Yes | [5 empty] | ΔT |  |  |  | #VALUE! |  | ℃ |  |  | Inlet |  | Mean |  | Outlet
|  |  |  | Vapor "x" |  |  |  | 0 | [5 empty] | Density |  |  |  | #VALUE! |  | kg/m3 |  |  | 0 |  | 0.15 |  | 0.3
|  |  |  | Flowrate |  |  |  | 1500 |  | kg/h
|  |  |  | Pressure |  |  |  | 7 |  | kg/cm2.g
|  |  |  | Fluid State |  |  |  | Sat. Liquid
|  |  | Property Data | [29 empty] | VBA
|  |  |  | Sat. Pressure |  |  |  | at | Twall | [12 empty] | #VALUE! |  |  | kg/cm2.g | [7 empty] | #VALUE!
|  |  |  | Pressure Difference | [9 empty] | ΔP | = | #VALUE! |  |  | #VALUE! |  | = | #VALUE! |  |  | kg/m2
|  |  |  | Latent Heat | [9 empty] | λ | [7 empty] | #VALUE! |  |  | kcal/kg
|  |  |  | Gravitational Acceleration Velocity | [9 empty] | g | = | 9.8066 |  |  | m/s2 |  | = | 127094184 |  |  | m/h2
Liquid Properties
[5 empty] | Density | [8 empty] | ρl | [7 empty] | #VALUE! |  |  | kg/m3
[5 empty] | Specific Heat | [8 empty] | Cl | [7 empty] | #VALUE! |  |  | kcal/kg.℃
[5 empty] | Viscosity | [8 empty] | μl | [7 empty] | #VALUE! |  |  | kg/mh |  | = | #VALUE! |  | cP
[5 empty] | Thermal Condutivity | [8 empty] | kl | [7 empty] | #VALUE! |  |  | kcal/m.h.℃
[5 empty] | Prandtl No. | [8 empty] | Prl | [7 empty] | #VALUE! |  |  | ---
[5 empty] | Surface tension | [8 empty] | σl | [7 empty] | #VALUE! |  |  | kg/m
Vapor Properties
[5 empty] | Density | [8 empty] | ρv | [7 empty] | #VALUE! |  |  | kg/m3
[5 empty] | Viscosity | [8 empty] | μv | [7 empty] | #VALUE! |  |  | kg/mh |  | = | #VALUE! |  | cP
|  |  | Tube ID | [10 empty] | ID |  | 43.8 |  | mm |  |  | = | 0.0438 |  |  | m
|  |  | Flow Area | [10 empty] | Afpi | [6 empty] | = | 0.0015067 |  |  | m2
|  |  | Velocity | [10 empty] | Vi | [6 empty] | = | #VALUE! |  |  | m/sec
Martinelli Correlation
Vapor "x"
|  |  |  | Mass Flow |  |  |  |  | m |  | 1500 |  | kg/h | [19 empty] | x | = |  | mv |  | = | 0.15
|  |  |  | Vapor "x" |  |  |  |  | x |  | 0.15 | [23 empty] | ml | + | mv
[18 empty] | Liquid | [5 empty] | Vapor
|  |  |  | Mass Flowrate |  |  |  |  | m | [6 empty] | ml |  | 1275 |  |  |  | mv |  | 225 | [8 empty] | VBA
|  |  |  | Mass Velocity |  |  |  |  | G | = | m | / | Afpi |  |  | Gl |  | 846198.1712 |  |  |  | Gv |  | 149329.089 | [8 empty] | #VALUE! |  |  |  | #VALUE!
|  |  |  | Reynolds No. |  |  |  |  | Re | = | G | ID | / | μ |  | Rel |  | #VALUE! |  |  |  | Rev |  | #VALUE! | [8 empty] | #VALUE! |  |  |  | #VALUE!
[33 empty] | #VALUE! |  |  |  | #VALUE!
|  |  | Martinelli Parameter | [5 empty] | X | = | f | ( | x | ρv | ρl | μl | μv | Rel | Rev | ) | [5 empty] | = | #VALUE! | [5 empty] | #VALUE! |  |  |  | #VALUE!
[9 empty] | Φ | = | [ | 1 | + | 21 | + | ( | 1 | ) ^ | 2 | ] ^ | 0.5 |  |  |  |  | = | #VALUE! | [5 empty] | #VALUE! |  |  |  | #VALUE!
[14 empty] | X |  |  | X
Chen Correlation
VBA
|  |  |  | h | = | S | hb | + | htp |  | = | #VALUE! |  | x | #VALUE! |  |  | + | #VALUE! | [6 empty] | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE!
Butterworth Equation
[5 empty] | Where, |  |  | S |  | Suppression Factor | [5 empty] | = | f | ( | Rel | , | F | ) |  |  |  | = | #VALUE! |  |  | --- |  |  | #VALUE! |  |  |  | S | = | [6 empty] | 1
[39 empty] | 1 | + | 2.53 |  | 1e-06 |  | ( | Rel | F | ^ | 1.25 |  | ) ^ | 1.17
[8 empty] | hb |  | Heat Transfer Coefficient in Nucleate Pool Boiling | [15 empty] | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE! |  |  |  |  | = | #VALUE!
[8 empty] | htp |  | in accordance with Dittus - Boelter Equation based on Liquid Properties | [26 empty] | Butterworth Equation
[10 empty] | = | kl | / | ID | x | 0.023 |  | x | Rel | ^ | 0.8 |  | x | Prl | ^ | 0.4 |  | x | F | [8 empty] | F | = | 2.35 |  | ( | 1 | + | 0.213 |  | ) ^ | 0.736
[26 empty] | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE! | [8 empty] | X
[10 empty] | Where, |  |  | F | Enhancement Factor | [5 empty] | = | Φ | ^ | 0.89 |  |  | = | #VALUE! |  |  | --- |  |  | #VALUE! |  |  |  |  | = | #VALUE!
Selected
[34 empty] | #VALUE! | [9 empty] | #VALUE! | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  | #VALUE! |  | #VALUE!
[34 empty] | Flow Regime |  | Rel |  |  | Rev |  |  | Martinelli Parameter
[34 empty] | 1 |  | > | 2000 |  | > | 2000 |  | Xtt | = |  |  | ( | 1 | - | x | ) ^ | 0.9 | ( | ρv | ) ^ | 0.5 | ( | μl | ) ^ | 0.1
[48 empty] | x |  |  |  |  | ρl |  |  |  | μv
[34 empty] | 2 |  | > | 2000 |  | < | 1000 |  | Xtl | = | 0.053479 |  | ( | 1 | - | x | ) ^ | 0.5 | ( | ρv | ) ^ | 0.5 | ( | μl | ) ^ | 0.5 | Rel ^ | 0.4
NTES | [31 empty] | Narai Thermal Engineering Services | [15 empty] | x |  |  |  |  | ρl |  |  |  | μv
[34 empty] | 3 |  | < | 1000 |  | > | 2000 |  | Xlt | = | 18.6548 |  | ( | 1 | - | x | ) ^ | 0.5 | ( | ρv | ) ^ | 0.5 | ( | μl | ) ^ | 0.5 | Rev ^ | -0.4
[48 empty] | x |  |  |  |  | ρl |  |  |  | μv
|  |  |  | Jakob No. |  |  |  | Ja | = | Cl | ΔT |  | = | #VALUE! | [19 empty] | 4 |  | < | 1000 |  | < | 1000 |  | Xll | = |  |  | ( | 1 | - | x | ) ^ | 0.5 | ( | ρv | ) ^ | 0.5 | ( | μl | ) ^ | 0.5
[10 empty] | λ | [37 empty] | x |  |  |  |  | ρl |  |  |  | μv
|  |  |  | Bond No. |  |  |  | Bo | = | g | ρl |  | = | #VALUE!
σl
|  |  |  | hb | = | 0.00122 | [6 empty] | kl | [6 empty] | prl | ^ | 0.21 | Ja | ^ | 0.24 | Bo | ^ | 0.5 | ΔP | ^ | 0.75
[8 empty] | ρl ^ | 0.01 |  | ρv ^ | 0.24 |  | g ^ | 0.25 |  | μl ^ | 0.5
Note on AJ4: Cell is filled !
1

## hnc
| Technical Material : | [21 empty] | Doc. No. |  |  |  | TM - HTC - 100
Heat Transfer Calculations | [22 empty] | Date |  |  |  | 2019. 5. 5.
[23 empty] | Revision |  |  |  | 0 | 1
[23 empty] | Sheet No. |  |  |  |  | 11 | of | 15
|  | 7. | Natural Convection
|  |  | H. T. Coefficient | [5 empty] | Tube |  |  |  | Horizontal |  |  |  | Outside |  |  |  | Facing Up
VBA
|  |  |  | hnc |  | = | kf | Nu | [16 empty] | = | #VALUE! |  |  | kcal/m2.h.℃ |  |  | #VALUE!
L
[6 empty] | Where, |  |  | kf |  | Thermal Condutivity at Film Temp. | [13 empty] | = | #VALUE! |  |  | kcal/m.h.℃
[9 empty] | L |  | Characteristic Length | [17 empty] | m
[11 empty] | Vertical Surface |  |  |  |  | : | Height | [6 empty] | H | = | 300 |  |  | mm
[11 empty] | Horizontal Cylinder |  |  |  |  | : | OD | [6 empty] | do | = | 50.8 |  |  | mm
[11 empty] | Horizontal Surface |  |  |  |  | : | A / P | [6 empty] | A/P | = | 83.35 |  |  | mm |  |  |  |  | V.S. | H.C.
|  |  | Nusselt No. | [13 empty] | A Area |  |  | P Perimeter | [12 empty] | a = | #VALUE! | #VALUE!
|  |  |  | Nu |  | = | a Ra^m |  |  | = | a ( Gr Prf )^m | [14 empty] | #VALUE! | [5 empty] | #VALUE! | m = | #VALUE! | #VALUE!
[6 empty] | Where, |  |  | a, m |  | Constant in Table 3.1
[9 empty] | Ra |  | Rayleigh No. | [13 empty] | = | #VALUE!
[9 empty] | Prf |  | Prandtl No. | [13 empty] | = | #VALUE!
Grashof No.
|  |  |  | Gr |  | = | L^3 ρf^2 g β ( Tw - Tb ) | [17 empty] | = | #VALUE! | [5 empty] | #VALUE!
μf^2
[6 empty] | Where, |  |  | ρf |  | Density at Film Temp. | [13 empty] | = | #VALUE! |  |  | kg/m3
[9 empty] | g |  | Gravitational Acceleration
[11 empty] | 9.8066 |  |  | m/s2 |  | = | 127094184 |  |  |  | m/h2
[9 empty] | β |  | Volumetric Expansion Coefficient | [17 empty] | 1/℃
[9 empty] | Tw |  | Wall Temp. | [13 empty] | = | #VALUE! |  |  | ℃
[9 empty] | Tb |  | Bulk Temp. | [13 empty] | = | #VALUE! |  |  | ℃
[9 empty] | μf |  | Viscosity at Film Temp. | [13 empty] | = | #VALUE! |  |  | kg/m.h
Volumetric Expansion Coefficient
|  |  |  | β |  | = | ρb - ρf |  |  |  | 1 | [13 empty] | = | #VALUE! | [5 empty] | #VALUE!
[7 empty] | ρf |  |  |  | Tf - Tb
[6 empty] | Where, |  |  | ρb |  | Density at Bulk Temp. | [13 empty] | = | #VALUE! |  |  | kg/m3
[9 empty] | Tf |  | Film Temp. |  |  | = | ( Tb + Tw ) / 2 | [9 empty] | = | #VALUE! |  |  | ℃
* Correction Factor for Vertical Tube
|  |  |  | D / L |  |  |  | = | 50.8 |  | / | 300 |  |  |  |  | = | 0.16933
|  |  |  | 35 / Gr^(1/4) |  |  |  | = | 35 |  | / | #VALUE! |  |  | ^(1/4) |  | = | #VALUE!
|  |  |  | K |  |  |  | = | 3 / 7 |  | Prf + 273 / 315 |  |  |  | ( | 15 ( Prf + 20 / 21 ) |  |  |  |  | ) | ^1/4 |  |  | = | #VALUE!
[11 empty] | Prf + 64 / 63 |  |  |  |  | Prf
|  |  |  | fh |  |  |  | = | 1 + K / ( D/L x Ra ^ ( |  |  |  |  | 0.25 |  | ) ) | [8 empty] | = | #VALUE!
VBA Application
|  |  | Fluid | [6 empty] | Cases
|  |  | Kind |  | Liquid |  |  |  |  | Plate |  |  | Tube |  |  | Tube |  |  | Tube |  |  | Plate |  | Plate
|  |  | Name |  | HFO 380 cSt |  |  |  |  | Vertical |  |  | Vertical |  |  | Vertical |  |  | Horizontal |  |  | Horizontal |  | Horizontal
|  |  | Press |  | 0 |  | kg/cm2.g | [5 empty] | Outside |  |  | Inside |  |  | Outside | [12 empty] | Sat. ? | No
|  |  | Tb |  | 50 |  | ℃ |  |  | Hgt | 300 |  | OD | 50.8 | [7 empty] | Facing Up |  | Facing Down | [7 empty] | Vapor "x" | 0
|  |  | Tw |  | 100 |  | ℃ | [5 empty] | t | 4
|  |  | H. T. Coefficient | [6 empty] | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  | #VALUE!
Table 3.1
|  |  | Configuration | [9 empty] | Ra = Gr Pr | [5 empty] | a |  |  | m
|  |  | Vertical Surface | [10 empty] | < | 10000 |  |  |  | 1.36 |  |  | 0.2
[14 empty] | < | 1000000000 |  |  |  | 0.59 |  |  | 0.25
[14 empty] | > | 1000000000 |  |  |  | 0.13 |  |  | 0.33333
|  |  | Horizontal Cylinder | [10 empty] | < | 1e-05 |  |  |  | 0.49 |  |  | 0
[14 empty] | < | 0.001 |  |  |  | 0.71 |  |  | 0.04
[14 empty] | < | 1 |  |  |  | 1.09 |  |  | 0.1
[14 empty] | < | 10000 |  |  |  | 1.09 |  |  | 0.2
[14 empty] | < | 1000000000 |  |  |  | 0.53 |  |  | 0.25
[14 empty] | > | 1000000000 |  |  |  | 0.13 |  |  | 0.33333
|  |  | Horizontal Surface |  |  |  |  | Hot |  | & | FU |  |  | < | 20000000 |  |  |  | 0.54 |  |  | 0.25
[8 empty] | Cold |  | & | FD |  |  | > | 20000000 |  |  |  | 0.14 |  |  | 0.33333
[8 empty] | Hot |  | & | FD | [7 empty] | 0.27 |  |  | 0.25
[8 empty] | Cold |  | & | FU
NTES | [30 empty] | Narai Thermal Engineering Services
Note on J13: Cell is filled !
Note on AJ4: Cell is filled !
1

## hrad
| Technical Material : | [20 empty] | Doc. No. |  |  |  | TM - HTC - 100
Heat Transfer Calculations | [21 empty] | Date |  |  |  | 2019. 5. 5.
[22 empty] | Revision |  |  |  | 0
[22 empty] | Sheet No. |  |  |  |  | 12 | of | 15
|  | 8. | Radiation
Surface Radiation
One Surface enclosed by the Other
[5 empty] | Vessel Surface Temperature | [5 empty] | 60 |  | ℃ |  |  | Ambient Air Temp. |  |  |  | 20 |  | ℃
[5 empty] | Vessel Surface Emissivity | [5 empty] | 0.9
Radiative Heat Transfer Coefficient
[6 empty] | hr | = | σ | ε | TKs^4 |  | - | TKa^4
[10 empty] | Ts |  | - | Ta
[7 empty] | = | 4.88e-08 |  |  | 0.9 |  | ( | #VALUE! |  | + | 273.15 | ) ^ | 4 | - | ( | #VALUE! |  | + | 273.15 |  | ) ^ | 4
[15 empty] | #VALUE! |  |  |  |  | - |  |  | #VALUE!
[7 empty] | = | #VALUE! |  |  | kcal/m2.h.℃
NTES | [29 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## +2
| Technical Material : | [20 empty] | Doc. No. |  |  | TM - HTC - 100
Heat Transfer Calculations | [21 empty] | Date |  |  | 2019. 5. 5.
[22 empty] | Revision |  |  | 0 | 1
[22 empty] | Sheet No. |  |  |  | 13 | of |  | 15
Gaseous Radiation
Fluid Properties
[9 empty] | Shell Side | [8 empty] | Tube Side
|  |  |  | Fluid |  |  |  |  | Flue Gas | [8 empty] | BFW |  | Steam | [10 empty] | Flue Gas
|  |  |  | Flowrate |  |  |  |  | 10000 | [5 empty] | Nm3/h | [15 empty] | Composition |  | volume% |  | volume%
|  |  |  | Pressure |  |  |  |  | 0 | [5 empty] | mmH2O |  |  | 10 |  |  |  | kg/cm2.g | [8 empty] | H2O |  | 5 |  | #VALUE!
[9 empty] | Inlet |  | Mean |  | Outlet |  |  |  |  | Inlet |  | Outlet | [10 empty] | CO2 |  | 10 |  | #VALUE!
|  |  |  | Temperature |  | Input |  | T | 1393 |  | 1213.5 |  | 1034 |  | ℃ |  |  | 60 |  | #VALUE! |  | ℃ | [8 empty] | N2 |  | 85 |  | #VALUE!
[6 empty] | Cal'd | [6 empty] | #VALUE! |  |  |  | Density | #VALUE! |  | #VALUE! |  | kg/m3 | [8 empty] | O2 |  | 0 |  | #VALUE!
|  |  |  | Wall Temp. |  | Input |  | Tw |  |  | 198 | [5 empty] | Enthalpy | #VALUE! |  | #VALUE! |  | kcal/kg | [8 empty] | SO2 |  | 0 |  | #VALUE!
[6 empty] | Cal'd |  |  |  |  | #VALUE!
Gaseous Radiative Heat Transfer Coefficient
|  |  |  | Beam Length |  |  |  | L | = | 4 x V / A | [13 empty] | = | 2 |  |  | m
|  |  |  | CO2 | [26 empty] | Total |  | 100 |  | #VALUE!
|  |  |  | Partial Pressure |  |  |  | Pc | = | Pt | x | v%CO2 |  | = | #VALUE! |  | x | #VALUE! | [5 empty] | = | #VALUE! |  |  | bar.g |  |  | M.W. | #VALUE!
[8 empty] | PcL | = | Pc | x | L |  | = | #VALUE! |  | x | 2 | [5 empty] | = | #VALUE! | [5 empty] | Density | #VALUE! |  | kg/Nm3
|  |  |  | Emissivity |  |  |  | εc | = | 0.7 | x | PcL^(1/3) |  |  |  | / | ( ( Tg + 273.15 ) / 100 )^.5 | [6 empty] | = | #VALUE!
[8 empty] | Rt | = | ( Tw + 273.15 ) / ( Tg + 273.15 ) | [13 empty] | = | 0.31692
[8 empty] | a0 | = | 0.7 | x | ( PcL x Rt )^(1/3) |  |  |  | / | ( ( Tw + 273.15 ) / 100 )^.5 | [6 empty] | = | #VALUE! | [5 empty] | Data for Emissivity |  |  |  | volume%
|  |  |  | Absorptivity |  |  |  | αc | = | a0 | / | Rt^.65 | [11 empty] | = | #VALUE! | [5 empty] | CO2 |  |  |  | #VALUE!
|  |  |  | H2O | [26 empty] | H2O |  |  |  | #VALUE!
|  |  |  | Partial Pressure |  |  |  | Pw | = | Pt | x | v%H2O |  | = | #VALUE! |  | x | #VALUE! | [5 empty] | = | #VALUE!
[8 empty] | PwL | = | Pw | x | L |  | = | #VALUE! |  | x | 2 | [5 empty] | = | #VALUE!
|  |  |  | Emissivity |  |  |  | εw | = | 7 | x | Pw^0.8 x L^0.6 | [5 empty] | / | ( ( Tg + 273.15 ) / 100 ) |  |  |  |  | = | #VALUE!
[8 empty] | a0 | = | 7 | x | ( Pw x Rt )^0.8 x L^0.6 | [5 empty] | / | ( ( Tw + 273.15 ) / 100 ) |  |  |  |  | = | #VALUE!
|  |  |  | Absorptivity |  |  |  | αw | = | a0 | / | Rt^.45 | [11 empty] | = | #VALUE!
Gas
|  |  |  | Emissivity |  |  |  | εg | = | εc | + | εw | - | εc | x | εw | x | fe | ( = | 1 |  | ) |  | = | #VALUE!
|  |  |  | Absorptivity |  |  |  | αg | = | αc | + | αw | - | αc | x | αw | x | fa | ( = | 0.39263 |  | ) |  | = | #VALUE!
|  |  |  | Surface Apsorptivity |  |  |  | αs | = | εs | / ( | εs | + | αg | - | εs | x | αg | ) |  |  |  |  | = | #VALUE! | [5 empty] | Wall Emissivity
[9 empty] | * | εs | = | Surface Emissivity |  |  |  |  | = | 0.85 | [12 empty] | 0.85
|  |  |  | hr | = | σ | αs | εg | TKg^4 |  | - | αg | TKw^4 | [10 empty] | = | #VALUE! |  |  | kcal/m2.h.℃
[9 empty] | Tg |  | - |  | Tw
[5 empty] | * | σ | = | Stefan - Boltzmann Constant | [6 empty] | = | 4.88e-08
|  |  | H. T. Rate |  | ( Overall H. T. Coefficient )
|  |  |  | Ud | = | 1 | / | [ | 1 |  | + | ro |  | + | tw |  | + | 1 |  | + | ri |  | ]
[9 empty] | hr | [5 empty] | kw |  |  | hi
[5 empty] | = | 1 | / | [ | 1 |  | + | 0.0005 |  | + | 0.005 |  | + | 1 |  | + | 0.0002 |  | ] | = | #VALUE! |  |  | kcal/m2.h.℃
[9 empty] | #VALUE! | [5 empty] | 40 |  |  | 10000
|  |  | Wall Temperatute |  |  |  |  | Tw | = | Tg - ( 1 / hr + ro ) x Ud x ( Tg - Ts ) | [13 empty] | = | #VALUE! |  |  | ℃
|  |  | Heat Transfer |  |  |  |  | H | = | hr |  | x | A |  | ( | Tg |  | - | Tw |  | )
[9 empty] | = | #VALUE! |  | x | 40 |  | ( | 1213.5 |  | - | #VALUE! |  | ) |  |  | = | #VALUE! |  |  | kcal/h
|  |  | Evaporation |  |  |  |  | W | = | H |  |  | / | ( | hv |  | - | hw |  | )
[9 empty] | = | #VALUE! |  |  | / | ( | #VALUE! |  | - | #VALUE! |  | ) |  |  |  | = | #VALUE! |  |  | kg/h
|  |  | Flue Gas Temp., Outlet | [5 empty] | Tgo |  | = | [12 empty] | = | #VALUE! |  |  | ℃
Gas Chamber
|  |  |  | Flue Gas | [16 empty] | Wall Thickness |  |  | tw |  | 5 |  | mm
[6 empty] | Velocity | [24 empty] | Density
[6 empty] | #VALUE! |  | m/sec |  |  |  | 2000 | [8 empty] | Volume |  |  | V |  | 20 |  | m3 |  |  | #VALUE! | kg/m3
[21 empty] | Surface Area |  |  | A |  | 40 |  | m2
[21 empty] | Beam Length |  |  | L |  | 2 |  | m
[8 empty] | 5000 | [7 empty] | 2000
NTES | [29 empty] | Narai Thermal Engineering Services
Note on N21: 아래와 같게 Input 요 !
Note on P19: 아래와 같게 Input 요 !
Note on AJ4: Cell is filled !
1

## U
| Technical Material : | [22 empty] | Doc. No. |  |  |  | TM - HTC - 100
Heat Transfer Calculations | [23 empty] | Date |  |  |  | 2018. 5. 10.
[24 empty] | Revision |  |  |  | 0
[24 empty] | Sheet No. |  |  |  |  | 14 | of |  | 15
|  | 9. | Overall Heat Transfer Coefficient
Plain Tube
|  |  |  | U | = | [8 empty] | 1 | [12 empty] | = | #VALUE! |  |  | kcal/m2.h.℃
[6 empty] | [ | ( | 1 | + | ro | ) |  | + | rw | + | ( | 1 | + | ri | ) | OD | ]
[8 empty] | ho | [8 empty] | hi |  |  |  | ID
MKH Unit
[5 empty] | Where, |  |  | U |  | Overall Heat Transfer Coefficient, Outside based
[8 empty] | ho |  | Film Coefficient of Shell Side Fluid | [11 empty] | 200 |  | kcal/m2.h.℃
[8 empty] | ro |  | Fouling Resistance on Outside Surface | [11 empty] | 0.0005 |  | m2.h.℃/kcal
[8 empty] | OD |  | Tube OD | [11 empty] | 50.8 |  | mm | 3.5 |  | t | [6 empty] | ASTM
[8 empty] | ID |  | Tube ID | [11 empty] | 43.8 |  | mm |  |  |  | Tube Thermal Cond. | [5 empty] | tube
[8 empty] | rw |  | Resistance of Tube Wall, Outside based | [11 empty] | #VALUE! |  | m2.h.℃/kcal |  |  |  | #VALUE! |  | kcal/m.h.℃ |  |  |  | A 210-A1
[8 empty] | hi |  | Film Coefficient of Tube Side Fluid | [11 empty] | 5000 |  | kcal/m2.h.℃ | [10 empty] | #VALUE!
[8 empty] | ri |  | Fouling Resistance on Inside Surface | [11 empty] | 0.0002 |  | m2.h.℃/kcal | [9 empty] | at | 98 | ℃
[8 empty] | Ao |  | Heat Transfer Surface Area, Outside | [11 empty] | 100 |  | m2
[8 empty] | Ai |  | Heat Transfer Surface Area, Inside | [11 empty] | 86.2205 |  | m2
|  |  | Overall Heat Transfer Coefficient, Clean | [11 empty] | * | ro | = | 0 | , | ri | = | 0
|  |  |  | Uc | = | [8 empty] | 1 | [12 empty] | = | #VALUE! |  |  | kcal/m2.h.℃
[6 empty] | [ | ( | 1 | + | 0 | ) | 1 | + | rw | + | ( | 1 | + | 0 | ) | OD | ]
[8 empty] | ho |  |  |  | 0 |  |  |  |  | hi |  |  |  | ID
Cleanliness Factor
|  |  |  | Fc | = | U | / | Uc | x | 100 |  | = | #VALUE! |  |  | / | #VALUE! |  |  | x | 100 | [5 empty] | = | #VALUE! |  |  | %
Wall Temperature
Tube Outside Wall Temperature
|  |  |  | Two |  | = | To | - | U | x | ( | 1 | + | ro | ) | x |  |  | ( | To | - | Ti | ) |  |  |  | = | #VALUE! |  |  | ℃
ho
Tube Inside Wall Temperature
|  |  |  | Twi |  | = | Ti | - | U | x | ( | 1 | + | ri | ) | x | Ao | x | ( | Ti | - | To | ) |  |  |  | = | #VALUE! |  |  | ℃
[12 empty] | hi |  |  |  |  | Ai
Heat Transfer Circuit
|  |  |  | To | 300 |  | ℃ | [8 empty] | Q | = | U | x | ( | To | - | Ti | ) | x | Ao | = | #VALUE! |  |  | kcal/h
[6 empty] | #VALUE! | [10 empty] | = | ho | x | ( | To | - | Tfo | ) | x | Ao | =
[6 empty] | Tfo |  | #VALUE! | [8 empty] | = | 1 | x | ( | Tfo | - | Two | ) | x | Ao | = | #VALUE!
|  |  |  | Heat Flow |  |  |  | Two | [9 empty] | ro
|  |  |  | Q | [9 empty] | Q |  |  | = | 1 | x | ( | Two | - | Twi | ) | x | Ao | = | #VALUE!
rw
[10 empty] | Twi | [6 empty] | = | 1 | x | ( | Twi | - | Tfi | ) | x | Ai | = | #VALUE!
[9 empty] | #VALUE! |  |  | Tfi | [5 empty] | ri
[11 empty] | #VALUE! |  |  | Ti | 80 | ℃ | = | hi | x | ( | Tfi | - | Ti | ) | x | Ai | = | #VALUE!
[5 empty] | Outside Fluid | Fouling |  | Surface Wall |  |  | Fouling |  | Inside Fluid
NTES | [32 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## _Fin
| Technical Material : | [21 empty] | Doc. No. |  |  |  | TM - HTC - 100
Heat Transfer Calculations | [22 empty] | Date |  |  |  | 2018. 5. 10.
[23 empty] | Revision |  |  |  | 0
[23 empty] | Sheet No. |  |  |  |  | 15 | of |  | 15
Finned Tube
|  |  | U | = | [8 empty] | 1 | [12 empty] | = | #VALUE! |  |  | kcal/m2.h.℃
[5 empty] | [ | ( | 1 | + | ro | ) | 1 | + | rw | + | ( | 1 | + | ri | ) | Ao | ]
[7 empty] | ho |  |  |  | η |  |  |  |  | hi |  |  |  | Ai
MKH Unit
|  |  |  | Where, |  |  | U |  | Overall Heat Transfer Coefficient, Outside based
[7 empty] | ho |  | Film Coefficient of Shell Side Fluid | [11 empty] | 200 |  | kcal/m2.h.℃
[7 empty] | ro |  | Fouling Resistance on Outside Surface | [11 empty] | 0.0005 |  | m2.h.℃/kcal
[7 empty] | η |  | Surface Efficiency, where appicable | [11 empty] | 0.606
[7 empty] | OD |  | Tube OD | [11 empty] | 50.8 |  | mm | 3.5 |  | t | [6 empty] | ASTM
[7 empty] | ID |  | Tube ID | [11 empty] | 43.8 |  | mm |  |  |  | Tube Thermal Cond. | [5 empty] | tube
[7 empty] | rw |  | Resistance of Tube Wall, Outside based | [11 empty] | #VALUE! |  | m2.h.℃/kcal |  |  |  | #VALUE! |  | kcal/m.h.℃ |  |  |  | A 210-A1
[7 empty] | hi |  | Film Coefficient of Tube Side Fluid | [11 empty] | 5000 |  | kcal/m2.h.℃ | [10 empty] | #VALUE!
[7 empty] | ri |  | Fouling Resistance on Inside Surface | [11 empty] | 0.0002 |  | m2.h.℃/kcal | [9 empty] | at | 149 | ℃
[7 empty] | Ao |  | Heat Transfer Surface Area, Outside | [11 empty] | 100 |  | m2
[7 empty] | Ai |  | Heat Transfer Surface Area, Inside | [11 empty] | 10 |  | m2 |  | * | Ao | / | Ai | = | 10
|  | Overall Heat Transfer Coefficient, Clean | [11 empty] | * | ro | = | 0 | , | ri | = | 0
|  |  | Uc | = | [8 empty] | 1 | [12 empty] | = | #VALUE! |  |  | kcal/m2.h.℃
[5 empty] | [ | ( | 1 | + | 0 | ) | 1 | + | rw | + | ( | 1 | + | 0 | ) | Ao | ]
[7 empty] | ho |  |  |  | η |  |  |  |  | hi |  |  |  | Ai
Cleanliness Factor
|  |  | Fc | = | U | / | Uc | x | 100 |  | = | #VALUE! |  |  | / | #VALUE! |  |  | x | 100 | [5 empty] | = | #VALUE! |  |  | %
Wall Temperature
Tube Outside Wall Temperature
|  |  | Two |  | = | To | - | U | x | ( | 1 | + | ro | ) | x | 1 |  | ( | To | - | Ti | ) |  |  |  | = | #VALUE! |  |  | ℃
[11 empty] | ho |  |  |  |  | η
Tube Inside Wall Temperature
|  |  | Twi |  | = | Ti | - | U | x | ( | 1 | + | ri | ) | x | Ao | x | ( | Ti | - | To | ) |  |  |  | = | #VALUE! |  |  | ℃
[11 empty] | hi |  |  |  |  | Ai
Heat Transfer Circuit
|  |  | To | 300 |  | ℃ | [8 empty] | Q | = | U | x | ( | To | - | Ti | ) | x | Ao | = | #VALUE! |  |  | kcal/h
[5 empty] | #VALUE! | [10 empty] | = | ho | η | ( | To | - | Tfo | ) | x | Ao | = | #VALUE!
[5 empty] | Tfo |  | #VALUE! | [8 empty] | = | η | x | ( | Tfo | - | Two | ) | x | Ao | = | #VALUE!
|  |  | Heat Flow |  |  |  | Two | [9 empty] | ro
|  |  | Q | [9 empty] | Q |  |  | = | 1 | x | ( | Two | - | Twi | ) | x | Ao | = | #VALUE!
rw
[9 empty] | Twi | [6 empty] | = | 1 | x | ( | Twi | - | Tfi | ) | x | Ai | = | #VALUE!
[8 empty] | #VALUE! |  |  | Tfi | [5 empty] | ri
[10 empty] | #VALUE! |  |  | Ti | 80 | ℃ | = | hi | x | ( | Tfi | - | Ti | ) | x | Ai | = | #VALUE!
|  |  |  | Outside Fluid | Fouling |  | Surface Wall |  |  | Fouling |  | Inside Fluid
NTES | [31 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## form
| Technical Material : |  |  |  | Doc. No. | TM - HTC - 100
Heat Transfer Calculations |  |  |  |  | Date | 2018. 5. 10.
[5 empty] | Revision | 0
[5 empty] | Sheet No. |  | x | of | 15
|  | x. | Aaaaaa
|  |  | x.1 | Aaaaaa
NTES | [9 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## 0
| Technical Material : |  |  | Doc. No. | TM - HTC - 100
Heat Transfer Calculations |  |  |  | Date | 2011. 1. 5.
|  |  |  | Revision | 0
|  |  |  | Sheet No. |  | 0 | of | 15
|  | 0. | Aaaaaa
NTES | [8 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1