## cover
|  |  |  | Doc. No. |  | TM - HTF - 100 |  |  | TM - HTF - 100
Technical Guide
|  |  | Technical Material | [5 empty] | Technical Material
Heat Transfer Fundamentals
`
sheetqty
|  |  |  | Total | 22 | sheets with a cover |  |  | 20
5
4
3
2
1 | 2019. 5. 5. | Updated. |  | S. J. Lee |  | Lee | LSJ
0 | 2008. 1. 10. | 1st Issue. |  | S. J. Lee |  | Lee | LSJ
Rev. | Date | Description |  | Prepared |  | Reviewed | Approved
나 래 열 기 술
Narai Thermal Engineering Services
| Homepage | www.ntes.co.kr |  | E-mail |  | ntes@ntes.co.kr
NTES | [7 empty] | Narai Thermal Engineering Services

## TOC
| Technical Material : |  |  |  | Doc. No. | TM - HTF - 100
Heat Transfer Fundamentals |  |  |  |  | Date | 2019. 5. 5.
[5 empty] | Rev. | 0
[5 empty] | Sheet No. |  | 1 | of | 1
T a b l e of C o n t e n t s
|  | 1. |  | Introduction
|  | 2. |  | Conduction
|  | 3. |  | Convection
|  |  | 3.1 | Forced Convection, Internal Flow
|  |  | 3.2 | Forced Convection, External Flow
|  |  | 3.3 | Condensation
|  |  | 3.4 | Boiling
|  |  | 3.5 | Natural Convection
|  | 4. |  | Radiation
|  | 5. |  | Overall Heat Transfer Coefficient
NTES | [9 empty] | Narai Thermal Engineering Services

## 1
| Technical Material : |  |  |  | Doc. No. | TM - HTF - 100
Heat Transfer Fundamentals |  |  |  |  | Date | 2019. 5. 5.
[5 empty] | Revision | 0
[5 empty] | Sheet No. |  | 1 | of | 20
|  | 1. | Introduction
Practical correlations for heat transfer calculations are summarized in this material.
References in english only are listed as below.
Fundamentals of Heat and Mass Transfer, 4th Edition, John Wiley & Sons
Engineering Heat Transfer, West Publishing Company
Perry's Chemical Engineers' Handbook, 7th Edition
Handbook of Heat Transfer, 3rd Edition, Mcgraw-hill
TEMA Standards, 9th Edition
Steam, its generation and use, Edition 41
NTES | [9 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## conduction
| Technical Material : | [16 empty] | Doc. No. | TM - HTF - 100
Heat Transfer Fundamentals | [17 empty] | Date | 2019. 5. 5.
[18 empty] | Revision | 0
[18 empty] | Sheet No. |  | 2 | of | 20
|  | 2. | Conduction
This is heat transfer from one part of a body to another part of the same body,
or from one body to another body in physical contact without displacement of the particles of the body.
Fourier's Law is the fundamental equation for steady state and one dimensional.
|  |  |  | q | = | - | k | dT
dx
[5 empty] | Where, |  |  | q |  | Heat Flux
Heat Transfer Rate per unit area normal to direction of heat flow
[8 empty] | k |  | Thermal Conductivity
[8 empty] | T |  | Temperature
[8 empty] | x |  | Distance in direction of heat flow
Temperature Profile in Plane Wall
T1
dT
T2
dx
Cylindrical Wall in Tube
[6 empty] | Ti |  | To | ID |  | OD
t
Equation
|  |  |  | q | = | - |  | 2 | k |  | dT
[7 empty] | OD | ln( OD / ID )
[5 empty] | Where, |  |  | OD |  | Tube OD
[8 empty] | ID |  | Tubd ID
[8 empty] | dT |  | = | Ti | - | To
[5 empty] | * | Wall Conductance |  |  |  |  | hw | = |  |  |  | 2 | k
[15 empty] | OD | ln( OD / ID )
[5 empty] | * | Wall Resistance |  |  |  |  | rw | = | 1 | = | OD | ln( OD / ID )
[13 empty] | hw |  |  | 2 | k
NTES | [22 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## convection
| Technical Material : | [20 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [21 empty] | Date |  |  |  | 2019. 5. 5.
[22 empty] | Revision |  |  |  | 0
[22 empty] | Sheet No. |  |  |  |  | 3 | of | 20
|  | 3. | Convection
This is heat transfer from one point to another point within a fluid, liquid or gas by mixing one portion of the fluid with another.
Newton's Law of Cooling is the fundamental equation.
|  |  |  | q | = | h | x | dT |  |  | Where, |  |  | q |  | Heat Flux
[14 empty] | h |  | Heat Transfer Coefficient
[14 empty] | T |  | Temperature
Dimensionless Group
Nusselt No.
|  |  |  | This is |  | : | the ratio of inertia to viscous force in the velocity boundary layer.
[5 empty] | Nu | = | h | D
k
Reynolds No.
|  |  |  | This is |  | : | the flow modulus proportional to the ratio of inertia to viscous force.
[5 empty] | Re | = | D | G |  |  |  | D | : | Charateristic Length |  |  |  | = | ID |  |  |  |  | for | Circular Conduit
[7 empty] | μ | [10 empty] | = | 4 | A | / | P |  | for | Non-circular Conduit
[20 empty] | A | : | Flow Corss-sectional Area
|  |  |  | Prandtl No. | [17 empty] | P | : | Wetted Perimeter
|  |  |  | This is |  | : | the ratio of momentum diffusivity to thermal diffusivity.
a measure of the relative effectivenss of momentum and energy transport by diffusion
in the velocity and thermal boundary layers.
[5 empty] | Pr | = | Cp | μ
k
Peclet No.
|  |  |  | This is |  | :
[5 empty] | Pe | = | Re | Pr
Graetz No.
|  |  |  | This is |  | :
[5 empty] | Gz | = | Re | Pr | D | = | Pe | D
[9 empty] | L |  |  | L
Grashof No.
|  |  |  | This is | : =: :; : Re: the ratio of buoancy force to viscous force in the velocity boundary layer.
[5 empty] | Gr | = | D^3 | ρ^2 | g | β | ( | Tw | - | Tb | )
μ^2
Rayleigh No.
[5 empty] | Ra | = | Gr | Pr
Correction Factor for Local Property Variation
Correlation by Kays-London
|  |  |  | Liquid | : Re: fh; : Pr: =; : D: ( μb / μw ); : D: ^ | p
|  |  |  | Vapor |  |  | fh | = | ( | Tb |  | + | 273.15 |  | ) ^ | p
273.15 | bar: : =; : D
[8 empty] | Where, |  |  | p Value
[14 empty] | Re | >= | 2300 |  | 2300 |  | > | Re
[13 empty] | Hot Fluid |  |  | Cold Fluid | Hot Fluid |  |  | Cold Fluid
[5 empty] | : Pe: Liquid | 0.25 |  |  | 0.11 | 0.14 |  |  | 0.14
[5 empty] | : Pe: Vapor | 0 |  |  | 0.5 | 0 |  |  | 0
NTES | [29 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## hic
| Technical Material : | [22 empty] | Doc. No. |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [23 empty] | Date |  |  | 2019. 5. 5.
[24 empty] | Revision |  |  | 0
[24 empty] | Sheet No. |  |  |  | 4 | of | 20
|  | 3.1 | Forced Convection, Internal Flow
Physical Mechanism
[5 empty] | Velocity Boundary Layer | [17 empty] | Entrance Length
Boundary Layer
ID
[11 empty] | δ | [11 empty] | Hydraulic Entrance Length
[23 empty] | Le | ~ | 0.0565 | Red
[5 empty] | Hydraulic Entrance Length | [11 empty] | Fully developed region | [5 empty] | ID
Temperature Boundary Layer
Thermal Entrance Length
[6 empty] | Ti |  |  |  | Ti |  |  |  | Tc | = | Ti |  |  | Tc | > | Ti |  | Uniform Surface Temperature
[23 empty] | Let | ~ | 0.037 | Red |  | Pr
[11 empty] | δT | [11 empty] | ID
Uniform Heat Flux
[5 empty] | Thermal Entrance Length | [7 empty] | Fully developed region | [9 empty] | Let | ~ | 0.053 | Red |  | Pr
ID
|  |  | Local Heat Transfer along Tube | [19 empty] | Where, |  | Le | Hydraulic Entrance Length
[25 empty] | ID | Tube ID
|  |  |  | Local Nusselt No. | [20 empty] | Red | Reynolds No.
[25 empty] | Let | Thermal Entrance Length
[25 empty] | Pr | Prandtl No.
[10 empty] | Re | : | Higher
[10 empty] | Re | : | Lower
|  |  |  | 0 | [14 empty] | x / d
Average Heat Transfer Correlation
Laminar Flow
|  |  |  | Condition |  |  | : | 2300 |  | >= | Re
[5 empty] | Gz | <= | 100 |  |  | * | Hausen Correlation
[5 empty] | Nu | = | 3.66 |  | + |  | 0.085 |  | x | Gz
[10 empty] | 1 + | 0.047 |  | x | Gz | ^ | ( 2 / 3 )
[5 empty] | Gz | > | 100 |  |  | * | Sieder and Tate Correlation
[5 empty] | Nu | = | 1.86 |  | x | Gz | ^ | ( 1 / 3 ) |  | x | 0
|  |  |  | Transitional Flow |  |  |  |  | * | Gnielinski Equation
|  |  |  | Condition |  |  | : | 2300 |  | < | Re | < | 10000
[5 empty] | Nu | = |  |  |  |  | f | / | 8 | x ( | Re | - | 1000 |  | ) x | Pr
[7 empty] | 1 + | 12.7 |  | x ( | f | / | 8 | ) ^ | 0.5 | x ( | Pr | ^ (2/3) |  | - | 1 | )
[6 empty] | Where, |  |  | Friction Factor
[9 empty] | f | = | ( | 0.79 |  | x | ln ( | Re | ) - | 1.64 |  | ) ^ | -2
|  |  |  | Turbulent Flow |  |  |  |  | * | Dittus - Boelter Equation
|  |  |  | Condition |  |  | : | Re | >= | 10000
[5 empty] | Nu | = | 0.023 |  | x | Re | ^ | 0.8 |  | x | Pr | ^ | n
[6 empty] | Where, |  |  | n |  | 0.4 |  | for |  | Cold Fluid to be heated
[11 empty] | 0.3 |  | for |  | Hot Fluid to be cooled
NTES | [30 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## hoc
| Technical Material : | [17 empty] | Doc. No. |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [18 empty] | Date |  |  | 2019. 5. 5.
[19 empty] | Revision |  |  | 0
[19 empty] | Sheet No. |  |  |  | 5 | of | 20
|  | 3.2 | Forced Convection, External Flow
Cross Flow over A Cylinder
D
Wake
V
Separation Point
Boundary Layer
Stagnation Point
Local Heat Transfer around A Cylinder
Local Nusselt No.
Angle from Stagnation Point
|  |  |  | 0 |  | 40 |  | 80 |  | 120 |  | 160 |  | degree
Hilpert Correlation
|  |  |  | Nu | = | C | Re | ^ | m | Pr | ^ | (1/3)
[5 empty] | Where, |  |  | Re | = | ρ | V | D | Re |  |  |  | C | m
[10 empty] | μ |  |  |  |  | ~ | 4 | 0.989 | 0.33
[13 empty] | 4 |  | ~ | 40 | 0.911 | 0.385
[13 empty] | 40 |  | ~ | 4000 | 0.683 | 0.466
[13 empty] | 4000 |  | ~ | 40000 | 0.193 | 0.618
[13 empty] | 40000 |  | ~ |  | 0.027 | 0.805
Zukauskas Correlation
|  |  |  | Nu | = | C | Re | ^ | m | Pr | ^ | n | [14 empty] | ( | Pr | / | Prw | ) ^ | 0.25
[5 empty] | Where, |  |  | Re | = | ρ | V | D | Re |  |  |  | C | m |  | Pr | <= | 10
[20 empty] | n | 0.37 | bar: Pr
[15 empty] | ~ | 40 | 0.75 | 0.4 |  | Pr | > | 10
[13 empty] | 40 |  | ~ | 1000 | 0.51 | 0.5 |  | n | 0.36
[13 empty] | 1000 |  | ~ | 200000 | 0.26 | 0.6
[13 empty] | 200000 |  | ~ |  | 0.076 | 0.7
NTES | [25 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## _plain
| Technical Material : | [21 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [22 empty] | Date |  |  |  | 2019. 5. 5.
[23 empty] | Revision |  |  |  | 0
[23 empty] | Sheet No. |  |  |  |  | 6 | of |  | 20
Flow across Tube Bank
|  |  | In-line | [11 empty] | Staggered
|  | Tube Arrangement | [18 empty] | SD
OD
[24 empty] | Gmax |  | = |  | ST |  | G0
[27 empty] | ST | - | OD
|  |  |  | ST | [11 empty] | ST
|  |  | G0 | [11 empty] | G0 | [8 empty] | Re |  | = | Gmax |  | OD
μ
[6 empty] | SL | [11 empty] | SL
Zukauskas Correlation
|  |  | Nu | = | C | Re | ^ | m | Pr | ^ | 0.36 | [21 empty] | ( | Pr | / | Prw | ) ^ | 0.25
|  |  |  | Where, |  |  | In-line | [10 empty] | Staggered
[7 empty] | Re | [6 empty] | C |  | m |  | Re | [6 empty] | C |  |  |  | m
[10 empty] | ~ | 100 |  |  | 0.9 |  | 0.4 |  |  |  |  | ~ | 500 |  |  | 1.04 |  |  |  | 0.4
[7 empty] | 100 |  |  | ~ | 1000 |  |  | 0.52 |  | 0.5 |  | 500 |  |  | ~ | 1000 |  |  | 0.71 |  |  |  | 0.5
[7 empty] | 1000 |  |  | ~ | 200000 |  |  | 0.27 |  | 0.63 |  | 1000 |  |  | ~ | 200000 |  |  | 0.35 (ST/SL)^0.2 |  |  |  | 0.6
[7 empty] | 200000 |  |  | ~ |  |  |  | 0.033 |  | 0.8 |  | 200000 |  |  | ~ |  |  |  | 0.031 (ST/SL)^0.2 |  |  |  | 0.8
Taborek Correlation
|  |  | Nu | = | C | Re | ^ | m | Pr | ^ | (1/3)
|  |  |  | Where, |  |  | In-line | [12 empty] | Staggered
[7 empty] | Re |  |  |  |  | a1 |  | a3 |  | a4 |  | m |  | Re |  |  |  |  | a1 |  | a3 |  | a4 |  | m
[9 empty] | ~ | 100 |  | 0.9 |  | 1.187 |  | 0.37 |  | 0.369 |  |  |  | ~ | 100 |  | 1.36 |  | 1.45 |  | 0.519 |  | 0.343
[7 empty] | 100 |  | ~ | 1000 |  | 0.408 | [5 empty] | 0.54 |  | 100 |  | ~ | 1000 |  | 0.593 | [5 empty] | 0.523
[7 empty] | 1000 |  | ~ | 10000 |  | 0.107 | [5 empty] | 0.734 |  | 1000 |  | ~ | 10000 |  | 0.321 | [5 empty] | 0.612
[7 empty] | 10000 |  | ~ |  |  | 0.37 | [5 empty] | 0.605 |  | 10000 |  | ~ |  |  | 0.321 | [5 empty] | 0.612
[7 empty] | C | = | a1 | ( | 1.33 |  | OD | ) ^ | ( | a3 | [6 empty] | )
[13 empty] | ST |  |  | 1 | + | 0.14 |  | Re | ^ | a4
Heat Transfer Coefficient
|  |  | h | = | k | / | OD | x | Nu | x | fh | x | Fd
|  |  |  | Where, |  |  | Fd |  | Depth Factor for No. of Tube Rows
NTES | [31 empty] | Narai Thermal Engineering Services
Depth Factor for No. of Tube Rows
|  |  | x: Staggered; Fd: 0.64 | 0.75 | 0.82 | 0.88 | 0.92 | 0.945 | 0.97 | 0.985 | 1
|  |  | x: In-line; Fd: 0.67 | 0.8 | 0.87 | 0.905 | 0.94 | 0.96 | 0.975 | 0.99 | 1
[10 empty] | No of Tube Rows |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Note on AJ4: Cell is filled !
1

## _finned
| Technical Material : | [21 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [22 empty] | Date |  |  |  | 2019. 5. 5.
[23 empty] | Revision |  |  |  | 0
[23 empty] | Sheet No. |  |  |  |  | 7 | of | 20
Circular Finned Tube
[18 empty] | Area Calculation |  |  |  |  | * | in | m2 | [6 empty] | Area
t
Area per 1 m Tube, Tube Inside
[9 empty] | ID |  | OD |  | Df |  |  |  |  | ai | = | π | x | ID | / | 1000
Area per 1 m Tube, Tube Outside, Bare
[18 empty] | ab | = | π | x | OD | / | 1000
[11 empty] | Hf | [6 empty] | Area per 1 m Tube, Fin
|  |  | tf |  |  | Pf | [11 empty] | af | = | [ π / 4 x |  |  | 2 x ( | Df | ^2 | - | OD | ^2 | )
[20 empty] | + | π | x |  | Df | x |  | tf | ] x | FPM | / 10^6
|  |  | Where, |  | OD |  | Tube OD | [10 empty] | Area per 1 m Tube, Tube Outside, Unfinned Surface
[5 empty] | t |  | Tube Thickness |  |  |  |  | ID |  | Tube ID |  |  |  | ar | = | π | x | OD | x ( | 1000 |  | - | tf | x | FPM | ) /10^6
[5 empty] | Hf |  | Fin Height |  |  |  |  | tf |  | Fin Thick |  |  |  | Area per 1 m Tube, Tube Outside
[5 empty] | Df |  | Fin OD |  |  |  |  | Pf |  | Fin Pitch |  |  |  | ao |  | = | af | + | ar
[5 empty] | FPI |  | Fin Q'ty per Inch | [10 empty] | Ratio of Area, Outside / Inside
[5 empty] | FPM |  | Fin Q'ty per Meter |  |  |  |  | * | in | mm |  |  |  | Raoi |  | = | ao | / | ai
Ratio of Area, Outside, Finned / Bare
[18 empty] | Raob |  | = | ao | / | ab
Tube Arrangement
|  |  | In-line | [8 empty] | Staggered
SD
[21 empty] | Gmax |  | = |  | ST |  | G0
[24 empty] | ST | - | OD
|  |  |  | ST | [8 empty] | ST
|  |  | G0 | [8 empty] | G0 | [8 empty] | Re |  | = | Gmax |  | OD
μ
[6 empty] | SL | [8 empty] | SL
|  | Briggs and Young Correlation | [7 empty] | * | for | Staggered
|  |  | Nu | = | 0.1378 |  | Re | ^ | 0.718 |  | Pr | ^ | (1/3) |  | ( | Pf - tf |  | ) ^ | 0.296 |  | ( | ST |  | ) ^ | 0.5
[16 empty] | Hf | [5 empty] | SD
|  | Schmidt Correlation | [7 empty] | * | Condition |  |  | : | 5 | < | af | / | ab | < | 12
In-line
|  |  | Nu | = | 0.3 |  | Re | ^ | 0.625 |  | Pr | ^ | (1/3) |  | ( | af |  | ) ^ | -0.375
ab
Staggered
|  |  | Nu | = | 0.45 |  | Re | ^ | 0.625 |  | Pr | ^ | (1/3) |  | ( | ao |  | ) ^ | -0.375
ab
Heat Transfer Coefficient
|  |  | h | = | k | / | OD | x | Nu | x | fh | x | Fd
|  |  |  | Where, |  |  | Fd |  | Depth Factor for No. of Finned Tube Rows
NTES | [30 empty] | Narai Thermal Engineering Services
Depth Factor for No. of Finned Tube Rows
|  |  | x: Finned Tube; Fd: 0.75 | 0.86 | 0.93 | 0.97 | 0.985 | 1
|  |  | x: No of Tube Rows; Fd: 1 | 2 | 3 | 4 | 5 | 6
Note on AJ4: Cell is filled !
1

## Feff
| Technical Material : | [21 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [22 empty] | Date |  |  |  | 2019. 5. 5.
[23 empty] | Revision |  |  |  | 0 | 1
[23 empty] | Sheet No. |  |  |  |  | 8 | of |  | 20
Fin Efficiency
|  |  | Circular Fin |  |  |  |  | * | Schmidt Empirical Solution | [7 empty] | * | McQuiston & Tree Approximate Method
|  |  |  | ηf | = | Actual Heat Transfer Rate from the Fin
Maximum Possible Heat Transfer Rate from the Fin
[5 empty] | = | tanh ( |  | m | he | ) | = | e ^ | ( m he ) |  | - | e ^ | ( - m he ) |  |  | x | 1
[8 empty] | m | he |  |  | e ^ | ( m he ) |  | + | e ^ | ( - m he ) |  |  |  | m | he
[5 empty] | Where, |  |  | m |  | Efficiency Parameter
[10 empty] | = | ( | 2 | ho | ) ^ | 0.5 |  |  | ho | = | 1 | / | ( | 1 | + | ro | )
[12 empty] | tf | kf | [9 empty] | ho
[8 empty] | he |  | Effective Fin Height
[10 empty] | = | Df | - | Dr | [ | 1 | + | 0.35 |  | ln( | Df | ) ] | = | Hf | [ | 1 | + | 0.35 |  | ln( | Df | ) ]
[12 empty] | 2 | [7 empty] | Dr | [9 empty] | Dr
Surface Efficiency
[5 empty] | ηs | = | Actual Heat Transfer Rate from the Surface
Maximum Possible Heat Transfer Rate from the Fin
[6 empty] | = | ( | ar | + | ηf | af | )
ao
[6 empty] | Where, |  |  | ar |  | Unfinned Surface Area
[9 empty] | af |  | Fin Surface Area
[9 empty] | ao |  | Total Surface Area
[11 empty] | = | ar | + | af
NTES | [31 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## hcd
| Technical Material : | [22 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [23 empty] | Date |  |  |  | 2019. 5. 5.
[24 empty] | Revision |  |  |  | 0 | 1
[24 empty] | Sheet No. |  |  |  |  | 9 | of |  | 20
|  | 3.3 | Condensation
Physical Mechanism in Vertical Plate
[6 empty] | Wall |  | Film
[12 empty] | Hot Fluid | [8 empty] | Condensing Load
[9 empty] | Laminar | [11 empty] | Γ | = | W
[14 empty] | Re | ~ | 30 | [6 empty] | p
|  |  | Cold Fluid | [6 empty] | Laminar, Wavy
[14 empty] | Re | ~ | 1800 |  |  |  |  | Reynolds No.
[21 empty] | Re | = | Dh ρf vf |  |  | = | 4 W |  | = | 4 | Γ
[10 empty] | Turbulent | [12 empty] | μf |  |  |  | p μf |  |  | μf
Temperature Profile
[10 empty] | Ts | [10 empty] | Ts |  | Sat. Temp. of Condensing Fluid
[8 empty] | Tw | [12 empty] | Tw |  | Wall Temp.
|  |  |  | Tc | [16 empty] | Tc |  | Cold Fluid Temp.
[21 empty] | Tf |  | Film Temp. |  |  | = | ( Ts + Tw ) / 2
Velocity and Temperature Profile
Shear Force
[8 empty] | δ |  |  |  | Weight |  | Buoyancy
[21 empty] | δ |  | Film Thickness
Velocity Profile
Temperature Profile
Boundary layer
|  |  |  | Analytical Relation for Laminar Flow on Vertical Plate | [13 empty] | * by Nusselt in 1916
[5 empty] | δ( x ) |  | = | [ | 4 μf kf ( Ts - Tw ) x | [5 empty] | ]^(1/4)
ρf ( ρf - ρv ) g λ
[5 empty] | q( x ) |  | = | h( x ) ( Ts - Tw ) |  |  |  | = | kf / δ( x ) ( Ts - Tw )
[5 empty] | h( x ) |  | = | kf / δ( x ) | [5 empty] | = |  |  | [ | kf^3 ρf ( ρf - ρv ) g λ | [5 empty] | ]^(1/4)
4 μf ( Ts - Tw ) x
[5 empty] | havg |  | = | 1 | ∫ | L | h( x ) dx |  |  | = | 0.943 |  | [ | kf^3 ρf ( ρf - ρv ) g λ | [5 empty] | ]^(1/4)
[8 empty] | L |  | 0 | [7 empty] | μf ( Ts - Tw ) L
[7 empty] | Where, |  |  | g |  | Gravitational Acceleration | [6 empty] | = | 9.8066 |  |  | m/s^2 |  | = | 127094184 |  |  | m/h^2
[10 empty] | ρf |  | Liquid Density at Film Temp. | [7 empty] | ρv |  | Vapor Density
[10 empty] | μf |  | Liquid Viscosity at Film Temp. | [7 empty] | kf |  | Liquid Thermal Conductivity at Film Temp.
[10 empty] | λ |  | Latent Heat
[10 empty] | h |  | Heat Transfer Coefficient
NTES | [32 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1
x
L

## _2
| Technical Material : | [17 empty] | Doc. No. |  | TM - HTF - 100
Heat Transfer Fundamentals | [18 empty] | Date |  | 2019. 5. 5.
[19 empty] | Revision |  | 0 | 1
[19 empty] | Sheet No. |  |  | 10 | of | 20
Physical Mechanism outside Horizontal Multi Tubes
1
2
Heat Transfer Coefficient
|  |  |  | N | : | No. of Tube Rows |  |  |  | hN | = | h1 | x | N | ^ ( | - 1 / 4 |  | )
[11 empty] | Where, |  | h1 |  | Heat Transfer Coefficient for a Single Tube
In-tube Condensation in Horizontal Tube
[9 empty] | A |  |  |  |  | B
|  |  | Vapor | Mist |  |  | Annular |  | Wavy |  | Stratified |  |  | Slug |  |  | Plug |  | Bubbly | Liquid
[9 empty] | A |  |  |  |  | B
[8 empty] | A - A |  |  |  | B - B
NTES | [24 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## _3
| Technical Material : | [18 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [19 empty] | Date |  |  |  | 2019. 5. 5.
[20 empty] | Revision |  |  |  | 0 | 1
[20 empty] | Sheet No. |  |  |  |  | 11 | of | 20
Condensing Load
|  | Γ | = | W
p
Reynolds No.
|  |  | Q | = | h A ( Ts - Tw ) |  |  | = | W λ
|  |  | Re | = | Dh ρf vf |  | = | 4 W |  | = | 4 | Γ | = | 4 h A ( Ts - Tw )
[5 empty] | μf |  |  | p μf |  |  | μf |  |  | p μf λ
Nusselt Equation
|  |  | Nu | = | h L | [13 empty] | Fluid Data
[5 empty] | kf | [15 empty] | Fluid Kind |  | Saturated
[21 empty] | Fluid Name |  | H2O | [5 empty] | Sat. ? | Yes
|  |  |  | Where, |  | h |  | Heat Transfer Coefficient | [12 empty] | Pressure |  | 7 |  |  | kg/cm2.g |  |  | Vapor "x" | 1
[6 empty] | A |  | Heat Transfer Area | [12 empty] | Sat. Temp., Ts |  | #VALUE! |  |  | ℃
[6 empty] | W |  | Condensed Flowrate | [12 empty] | Tw |  | 165 |  |  | ℃
[6 empty] | λ |  | Latent Heat | [12 empty] | ( Tb + Tw ) / 2 = Tf |  | #VALUE! |  |  | ℃
[6 empty] | Dh |  | Hydraulic Diameter of Condensate Flow | [12 empty] | λ |  | #VALUE! |  |  | kcal/kg
[6 empty] | vf |  | Average Velocity of Condensate | [12 empty] | ρv |  | #VALUE! |  |  | kg/m3
[6 empty] | p |  | Wetted Perimeter of Condensate | [12 empty] | ρf |  | #VALUE! |  |  | kg/m3
[6 empty] | L |  | Characteristic Length | [12 empty] | μf |  | #VALUE! |  |  | kg/m.h
[6 empty] | kf |  | Fluid Thermal Conductivity at Film Temp. | [12 empty] | kf |  | #VALUE! |  |  | kcal/m.h.℃
[21 empty] | g |  | 127094184 |  |  | m/h^2 |  |  | 9.8066 |  | m/s^2
Anaylitical Equations
|  | Geometry |  |  |  |  | Character- |  |  | Equation | [11 empty] | Predition
istic Length
|  |  | Vertical Plate | [7 empty] | h | = | 0.943 |  | [ | kf^3 ρf ( ρf - ρv ) g λ |  |  |  | ]^(1/4) |  |  | W | = | 10 |  | kg/h
[16 empty] | μf ( Ts - Tw ) L | [6 empty] | H | = | 1000 |  | mm
[11 empty] | Γ | = | W |  | Re | = | 4 | Γ
|  |  | H |  |  |  |  | H |  |  |  |  | H |  |  |  | μf | [5 empty] | Γ | = | 10 |  | kg/h.m
[11 empty] | h | = | 1.47 |  | Re^(-1/3) |  | [ | μf^2 | ]^(-1/3) |  |  |  | Re | = | #VALUE!
[18 empty] | kf^3 ρf^2 g |  |  |  |  | h | = | #VALUE!
|  | Vertical Cylinder | [8 empty] | h | = | 0.943 |  | [ | kf^3 ρf ( ρf - ρv ) g λ |  |  |  | ]^(1/4) |  |  | D | = | 25.4 |  | mm
μf ( Ts - Tw ) L
[11 empty] | Γ | = | W |  | Re | = | 4 | Γ |  |  |  |  | Γ | = | 125.3189 |  | kg/h.m
|  |  | L |  |  |  |  | π D |  |  |  |  | π D |  |  |  | μf | [5 empty] | Re | = | #VALUE!
[6 empty] | D |  |  |  |  | h | = | 1.47 |  | Re^(-1/3) |  | [ | μf^2 | ]^(-1/3)
[18 empty] | kf^3 ρf^2 g |  |  |  |  | h | = | #VALUE!
|  | Horizontal Cylinder | [8 empty] | h | = | 0.728 |  | [ | kf^3 ρf ( ρf - ρv ) g λ |  |  |  | ]^(1/4) |  |  | L | = | 1000 |  | mm
μf ( Ts - Tw ) D
[5 empty] | L | [5 empty] | Γ | = | W |  | Re | = | 4 | Γ |  |  |  |  | Γ | = | 10 |  | kg/h.m
[8 empty] | L |  |  |  |  | L |  |  |  | μf | [5 empty] | Re | = | #VALUE!
|  |  | D | [7 empty] | h | = | 1.51 |  | Re^(-1/3) |  | [ | μf^2 | ]^(-1/3)
[18 empty] | kf3 ρf^2 g |  |  |  |  | h | = | #VALUE!
|  |  | Tube Inside | [19 empty] | ID | = | 19.86 |  | mm
[11 empty] | h | = | 0.815 |  | [ | kf^3 ρf ( ρf - ρv ) g λ |  |  |  | ]^(1/4)
|  | ID | [5 empty] | ID | [7 empty] | μf ( Ts - Tw ) π ID | [6 empty] | h | = | #VALUE!
NTES | [27 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## _4
| Technical Material : | [19 empty] | Doc. No. | TM - HTF - 100
Heat Transfer Fundamentals | [20 empty] | Date | 2018. 5. 10.
[21 empty] | Revision | 0
[21 empty] | Sheet No. |  | 12 | of | 20
|  | Tube Bank |  |  |  |  | * | Practical Equations by | [5 empty] | Devore
Vertical Tubes
Condensing Load
[5 empty] | Γ | = | W | [5 empty] | OD |  | Tube OD
[7 empty] | π | OD | Nt |  |  |  | Nt |  | Tube Q'ty
|  |  |  | Reynolds No. | [5 empty] | * | Condition |  |  | : | Laminar Flow |  |  | Γ | <= | 2300
[5 empty] | Re | = | 4 | Γ
μf
Heat Transfer Coefficient
|  |  |  | h | = | 1.47 |  | Re^(-1/3) |  | [ | μf^2 |  |  | ]^(-1/3)
kf^3 ρf^2 g
Horizontal Tubes
Condensing Load
[5 empty] | Γ | = | W
[7 empty] | Le | ns
[6 empty] | Where, |  |  | ns |  | Equivalent Tube Q'ty
Tube Pattern
[11 empty] | = | 2.08 |  | Nt | ^ | 0.495 | for |  | Triangular
[11 empty] | = | 1.022 |  | Nt | ^ | 0.519 | for |  | Rotated Triangular
[11 empty] | = | 1.288 |  | Nt | ^ | 0.48 | for |  | Square
[11 empty] | = | 1.37 |  | Nt | ^ | 0.518 | for |  | Rotated Square
|  |  |  | Reynolds No. | [5 empty] | * | Condition |  |  | : | Laminar Flow |  |  | Γ | <= | 2300
[5 empty] | Re | = | 4 | Γ
μf
Heat Transfer Coefficient
|  |  |  | h | = | 1.51 |  | Re^(-1/3) |  | [ | μf^2 |  |  | ]^(-1/3)
kf^3 ρf^2 g
NTES | [25 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## hboil
| Technical Material : | [22 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [23 empty] | Date |  |  |  | 2019. 5. 5.
[24 empty] | Revision |  |  |  | 0 | 1
[24 empty] | Sheet No. |  |  |  |  | 13 | of |  | 20
|  | 3.4 | Boiling
Pool Boiling
Boiling Curve
Heat Flux
CHF ( Critical Heat Flux )
Maximum Heat Flux Point in Nucleat Boiling
ONB
Onset of
Nucleate Boiling
Minimum Heat Flux Point in Film Boiling
Temperaure Difference
[8 empty] | *1 |  | *2 |  | *3
[8 empty] | Region |  |  | Boiling Mode
[8 empty] | *1 |  |  | Nucleate Boiling
[8 empty] | *2 |  |  | Transition Boiling
[8 empty] | *3 |  |  | Film Boiling
Dimensionless Group
Jakob No.
[5 empty] | This is |  | : | the ratio of the maximum sensible energy absorbed by the vapor to the latent energy absorbed by the vapor.
[6 empty] | Ja | = | Cl | ΔT
λ
Bond No.
[5 empty] | This is |  | : | the ratio of the gravitational body force to the surface tension force.
[6 empty] | Bo | = | g | ρl
σl
General Nusselt No. Equation
[5 empty] | NuL |  | = | f [ | ρ | g | ( | ρl | - | ρv | ) | L^3 | , | Pr | , | Ja | , | Bo | ]
μ^2
Nucleate Boiling
[5 empty] | Foster and Zuber Correlation | [8 empty] | * | Fluid Property based Method
Dimensional Form
[6 empty] | hb | = | 0.00122 |  | ( | kl ^ | 0.79 |  | Cl ^ | 0.45 |  | ρl ^ | 0.49 |  | g ^ | 0.25 |  | ) | ΔT | ^ | 0.24 |  | ΔP | ^ | 0.75
[11 empty] | σl ^ | 0.5 |  | μl ^ | 0.29 |  | λ ^ | 0.24 |  | ρv ^ | 0.24
Dimensionless Form
[6 empty] | hb | = | 0.00122 | [6 empty] | kl | [6 empty] | Prl | ^ | 0.21 | Ja | ^ | 0.24 | Bo | ^ | 0.5 | ΔP | ^ | 0.75
[10 empty] | ρl ^ | 0.01 |  | ρv ^ | 0.24 |  | g ^ | 0.25 |  | μl ^ | 0.5
[5 empty] | Mostinski Equation | [8 empty] | * | Reduced Pressure based Method
[6 empty] | hb | = | Z1 | ( | ΔT | ) ^ | 2.33
Where,
[7 empty] | Z1 | = | [ | 0.1 | Pc | ^ | 0.69 | ( | 1.8 | R | ^ | 0.17 | + | 4 | R | ^ | 1.2 | + | 10 | R | ^ | 10 | ) | ] ^ | 3.33
[8 empty] | Where, |  |  | Pc |  | Critical Pressure |  |  |  |  | kg/cm2.a
[11 empty] | R |  | Reduced Pressure |  |  |  |  | = | P | / | Pc
NTES | [32 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## .2
| Technical Material : | [21 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [22 empty] | Date |  |  |  | 2019. 5. 5.
[23 empty] | Revision |  |  |  | 0 | 1
[23 empty] | Sheet No. |  |  |  |  | 14 | of | 20
Nucleate Boiling, continued
|  |  | Tube Bundle Effect | [5 empty] | * | Taborek |  |  |  | h | = | Fb | x | hb
Correction Factor
|  |  |  | Fb | = | 1 | + | 0.1 |  | [ |  |  | 0.785 |  | Db |  |  |  | - | 1 | ]
[11 empty] | C1 | ( | pt | / | OD | ) ^ | 2 | OD | [6 empty] | Tube Pattern
[5 empty] | Where, |  |  | OD |  | Tube OD | [5 empty] | Constant |  |  | C1 | = | 0.866 |  | for |  | Triangular
[8 empty] | pt |  | Tube Pitch | [10 empty] | 0.866 |  | for |  | Rotated Triangular
[8 empty] | Db |  | Bundle Diameter | [10 empty] | 1 |  | for |  | Square
[21 empty] | 1 |  | for |  | Rotated Square
CHF ( Critical Heat Flux )
Zuber Correlation
|  |  |  | qmax |  | = | π | λ | ρv | [ | σ | g | gc | ( | ρl | - | ρv | ) | ] ^ | 0.25 |  | ( | ρl | + | ρv | ) ^ | 0.5
[7 empty] | 24 | [5 empty] | ρv | ^ | 2 | [8 empty] | ρl
Minimum Heat Flux
Zuber Correlation
|  |  |  | qmin |  | = | π ^ | 2 | ( | 4 | ) ^ | 0.25 |  | λ | ρv | [ | σ | g | gc | ( | ρl | - | ρv | ) | ] ^ | 0.25
[7 empty] | 60 |  |  | 3 | [7 empty] | ( | ρl | + | ρv | ) ^ | 2
Transitional Boiling
Later
Film Boiling
Later
NTES | [30 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## .3
| Technical Material : | [10 empty] | Doc. No. | TM - HTF - 100
Heat Transfer Fundamentals | [11 empty] | Date | 2019. 5. 5.
[12 empty] | Revision | 0 | 1
[12 empty] | Sheet No. |  | 15 | of | 20
Forced Convection Boiling
Vertical Tube Inside
Flow Regime
[7 empty] | Vapor |  | Boiling Mode
[7 empty] | Mist |  | Post-DNB Boiling
DNB
Departure from Nucleate Boiling
[7 empty] | Annular |  | Flow Boiling
Slug
Nucleate Boiling
Bubbly
Liquid
Heat Transfer Coefficient
Horizontal Tube Inside
|  |  |  | Liquid | Bubbly | Slug |  | Annualar |  | Mist | Vapor
CHF ( Critical Heat Flux )
Later
Correlation for Post-CHF Heat Transfer
Later
NTES | [16 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## .4
| Technical Material : | [21 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [22 empty] | Date |  |  |  | 2019. 5. 5.
[23 empty] | Revision |  |  |  | 0 | 1
[23 empty] | Sheet No. |  |  |  |  | 16 | of |  | 20
Two Phase Flow
Martinelli Correlation
[8 empty] | Liquid | [5 empty] | Vapor | [5 empty] | Vapor Quality
|  |  |  | Mass velocity |  |  |  | Gl |  | = | ml |  |  | Gv |  | = | mv |  |  | x | = |  | mv
[11 empty] | Afpi | [5 empty] | Afpi |  |  |  |  | ml | + | mv
|  |  |  | Reynolds No. |  |  |  | Rel |  | = | Gl | ID |  | Rev |  | = | Gv | ID |  | ml | = | 1 | - | x
[11 empty] | μl | [5 empty] | μv |  |  | mv |  |  | x
|  |  |  | Flow Regime |  | Rel |  |  | Rev |  |  | Martinelli Parameter
|  |  |  | 1 |  | > | 2000 |  | > | 2000 |  | Xtt | = |  |  | ( | 1 | - | x | ) ^ | 0.9 | ( | ρv | ) ^ | 0.5 | ( | μl | ) ^ | 0.1
[18 empty] | x |  |  |  |  | ρl |  |  |  | μv
|  |  |  | 2 |  | > | 2000 |  | < | 1000 |  | Xtl | = | 0.053479 |  | ( | 1 | - | x | ) ^ | 0.5 | ( | ρv | ) ^ | 0.5 | ( | μl | ) ^ | 0.5 | Rel ^ |  | 0.4
[18 empty] | x |  |  |  |  | ρl |  |  |  | μv
|  |  |  | 3 |  | < | 1000 |  | > | 2000 |  | Xlt | = | 18.6548 |  | ( | 1 | - | x | ) ^ | 0.5 | ( | ρv | ) ^ | 0.5 | ( | μl | ) ^ | 0.5 | Rev ^ |  | -0.4
[18 empty] | x |  |  |  |  | ρl |  |  |  | μv
|  |  |  | 4 |  | < | 1000 |  | < | 1000 |  | Xll | = |  |  | ( | 1 | - | x | ) ^ | 0.5 | ( | ρv | ) ^ | 0.5 | ( | μl | ) ^ | 0.5
[18 empty] | x |  |  |  |  | ρl |  |  |  | μv
|  |  |  | Vapor Vol. Fraction | [5 empty] | Rv | = | 1 | - | ( |  |  |  | 1 |  |  |  | ) ^ |  |  | = | 1 | - | 1
[16 empty] | 1 |  | + | 21 | + | 1 |  | 0.5 |  |  |  |  | Φ
[15 empty] | X | ^ | 2 |  | X
|  |  |  | Liquid Vol. Fraction | [5 empty] | Rl | = | 1 | - | Rv
Chen Correlation
|  |  | h | = | S | hb | + | htp
Butterworth Equation
|  |  |  | Where, |  |  | S |  | Suppression Factor | [5 empty] | = | f | ( | Rel | , | F | ) | [11 empty] | S | = | [6 empty] | 1
[7 empty] | hb |  | Heat Transfer Coefficient in Nucleate Pool Boiling | [25 empty] | 1 | + | 2.53 |  | 1e-06 |  | ( | Rel | F | ^ | 1.25 | ) ^ | 1.17
[7 empty] | htp |  | in accordance with Dittus - Boelter Equation based on Liquid Properties
[9 empty] | = | kl | / | ID | x | 0.023 |  | x | Rel | ^ | 0.8 |  | x | Prl | ^ | 0.4 |  | x | F
Butterworth Equation
[9 empty] | Where, |  |  | F | Enhancement Factor | [5 empty] | = | Φ | ^ | 0.89 | [10 empty] | F | = | 2.35 |  | ( | 1 | + | 0.213 |  | ) ^ | 0.736
[17 empty] | Where, |  |  | Φ | ^ | 2 | = | 1 | + | 21 | + | ( | 1 | ) ^ | 2 | [6 empty] | X
[26 empty] | X |  |  | X
NTES | [30 empty] | Narai Thermal Engineering Services
[8 empty] | S |  | 0.9 | 0.8 | 0.62 | 0.5 | 0.41 | 0.36 | 0.2 | 0.1 | 0.09
[8 empty] | Rel x F^1.25 |  | 10000 | 20000 | 40000 | 60000 | 80000 | 100000 | 200000 | 400000 | 600000
Note on AJ4: Cell is filled !
1

## hnc
| Technical Material : | [14 empty] | Doc. No. |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [15 empty] | Date |  |  | 2019. 5. 5.
[16 empty] | Revision |  |  | 0 | 1
[16 empty] | Sheet No. |  |  |  | 17 | of | 20
|  | 3.5 | Natural Convection
Physical Mechanism
[6 empty] | Wall |  | Film
Turbulent
|  |  |  | Hot Fluid | [6 empty] | Cold Fluid
Laminar
Temperature Profile
|  |  |  | Th | [11 empty] | Th | Hot Fluid Temp.
[8 empty] | Tw | [7 empty] | Tw | Cold Fluid Wall Temp.
[10 empty] | Tb | [5 empty] | Tb | Cold Fluid Temp.
Volumetric Expansion Coefficient
[15 empty] | Where, | ρb | Fluid Density at Tb
|  |  |  | β | = | - | 1 | Δρ | = |  | 1 | ρb - ρf |  |  |  | ρf | Fluid Density at Tf
[7 empty] | ρ | ΔT |  |  | ρf | Tf - Tb |  |  |  | Tf | Film Temp.
[17 empty] | = | ( Tw + Tb ) / 2
|  |  | Grashof Number | [11 empty] | Where, | g | Gravitational Acceleration
[17 empty] | = | 9.8066 |  |  | m/s^2
|  |  |  | Gr | = | Buoyancy Force |  |  |  |  | = | g Δρ V | = | g β ΔT V |  |  | = | 127094184 |  |  | m/h^2
[6 empty] | Viscous Force | [5 empty] | ρ ν2 |  | ν2 |  | V | Volume
[16 empty] | ν | Kinematic Viscosity
[5 empty] | = | L^3 ρf^2 g β ( Tw - Tb ) | [10 empty] | = μ / ρ
[6 empty] | μf2 | [9 empty] | L | Characteristic Length
[16 empty] | μf | Absolute Viscosity
Velocity and Temperature Profile
Temperature Profile
Velocity Profile
Boundary Layer
NTES | [22 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## +2
| Technical Material : | [19 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [20 empty] | Date |  |  |  | 2019. 5. 5.
[21 empty] | Revision |  |  |  | 0 | 1
[21 empty] | Sheet No. |  |  |  |  | 18 | of | 20
Nusselt Equation
|  |  | Nu | = | h L | = | C ( Gr Prf )^n |  |  | = | C Ra^n | [8 empty] | Fluid Data
[5 empty] | kf | [16 empty] | Fluid Kind |  | Liquid
|  |  |  | Where, |  |  | h |  | Heat Transfer Coefficient | [12 empty] | Fluid Name |  | HFO 380 cSt | [5 empty] | Sat. ? | No
[7 empty] | kf |  | Fluid Thermal Conductivity at Film Temp. | [12 empty] | Pressure |  | 0 |  |  | kg/cm2.g |  |  | Vapor "x" | 0
[7 empty] | C |  | Constant | [12 empty] | Temperature, Tb |  | 50 |  |  | ℃
[7 empty] | Prf |  | Fluid Prandtl No. at Film Temp. | [12 empty] | Tw |  | 100 |  |  | ℃
[7 empty] | n |  | Exponent | [12 empty] | ( Tb + Tw ) / 2 = Tf |  | 75 |  |  | ℃
[7 empty] | Ra |  | Rayleigh No. | [12 empty] | ρb |  | #VALUE! |  |  | kg/m3
[9 empty] | Critical Ra |  | ~ | 1000000000 |  | for Vertical Plate | [7 empty] | ρf |  | #VALUE! |  |  | kg/m3
[7 empty] | g |  | Gravitational Acceleration | [12 empty] | β |  | #VALUE! |  |  | 1/℃
[9 empty] | 9.8066 |  | m/s^2 |  | = | 127094184 |  |  | m/h^2 |  |  |  |  | Prf |  | #VALUE!
[22 empty] | μf |  | #VALUE! |  |  | kg/m.h
|  | Empirical Correlations | [19 empty] | kf |  | #VALUE! |  |  | kcal/m.h.℃
|  | Geometry | [5 empty] | Character- |  | Range of Ra |  |  |  |  | Nu Equation | [7 empty] | Predition
istic Length
[24 empty] | H = |  | 300 |  | mm
|  |  | Vertical Plate | [20 empty] | Gr = |  | #VALUE!
[24 empty] | Ra = |  | #VALUE!
[12 empty] | ~ | 10000 |  |  | 1.36 |  | Ra ^ | 0.2 |  |  |  | Nu = |  |  | #VALUE!
|  |  | H |  |  | Q |  |  | H | 10000 |  | ~ | 1000000000 |  |  | 0.59 |  | Ra ^ | 0.25 | [6 empty] | #VALUE!
[10 empty] | 1000000000 |  | ~ | 10000000000000 |  |  | 0.13 |  | Ra ^ | 0.33333 | [6 empty] | #VALUE!
[24 empty] | h = |  | #VALUE!
[10 empty] | 0.1 |  | ~ | 1000000000 |  | 0.68 + |  | 0.67 Ra1/4
[17 empty] | ( 1 + ( 0.492 / Pr )9/16 )4/9 | [5 empty] | Nu = |  |  | #VALUE!
[10 empty] | 1000000000 |  | ~ | 1000000000000 |  | { 0.825 + |  | 0.387 Ra1/6 |  |  |  |  | }2 |  |  |  | #VALUE!
[17 empty] | ( 1 + ( 0.492 / Pr )9/16 )8/27 | [6 empty] | h = |  | #VALUE!
|  |  | Inclined Plate | [20 empty] | Θ = |  | 45 |  | deg
|  |  |  | Θ |  | Q | [17 empty] | Gr = |  | #VALUE!
[9 empty] | L |  |  | *** |  |  |  | g cos Θ to replace g | [7 empty] | Ra = |  | #VALUE!
|  |  | L | [20 empty] | Nu = |  | #VALUE!
[24 empty] | h = |  | #VALUE!
Horizontal Plate
|  | Hot Surface, Upward | [21 empty] | D = |  | 333 |  | mm
|  | Cold Surf., Downward | [21 empty] | A / p = |  | 83.25
[24 empty] | Gr = |  | #VALUE!
|  |  |  | Q | [19 empty] | Ra = |  | #VALUE!
[9 empty] | A / p | 10000 |  | ~ | 20000000 |  |  | 0.54 |  | Ra ^ | 0.25 |  |  |  | Nu = |  |  | #VALUE!
[10 empty] | 20000000 |  | ~ | 100000000000 |  |  | 0.14 |  | Ra ^ | 0.33333 | [6 empty] | #VALUE!
|  |  |  | D |  |  |  | = | D / 4 | [14 empty] | h = |  | #VALUE!
Hot Surf., Downward
Cold Surface, Upward
[10 empty] | 100000 |  | ~ | 100000000000 |  |  | 0.27 |  | Ra ^ | 0.25 |  |  |  |  | Nu = |  | #VALUE!
[24 empty] | h = |  | #VALUE!
Q
|  | Vertical Cylinder | [21 empty] | L = |  | 300 |  | mm
[16 empty] | Vertical Plate when | [7 empty] | D = |  | 50.8 |  | mm
[16 empty] | D ≥ 35 L / Gr1/4 | [7 empty] | Gr = |  | #VALUE!
|  |  | L | [20 empty] | Ra = |  | #VALUE!
[7 empty] | D |  | L | [6 empty] | When D ＜ 35 L / Gr1/4 , | [7 empty] | Nu = |  | #VALUE!
[16 empty] | correction factor applies | [7 empty] | h = |  | #VALUE!
[16 empty] | to Nu for Vertical Plate. | [7 empty] | 35L/Gr1/4 = |  | #VALUE! |  | mm
[24 empty] | D = |  | 50.8 |  | mm
|  | Horizontal Cylinder | [21 empty] | Gr = |  | #VALUE!
[24 empty] | Ra = |  | #VALUE!
[12 empty] | ~ | 1 |  |  | 1.09 |  | Ra ^ | 0.1 |  |  |  | Nu = |  |  | #VALUE!
|  |  | D | [6 empty] | 1 |  | ~ | 10000 |  |  | 1.09 |  | Ra ^ | 0.2 | [6 empty] | #VALUE!
[9 empty] | D | 10000 |  | ~ | 1000000000 |  |  | 0.53 |  | Ra ^ | 0.25 | [6 empty] | #VALUE!
[10 empty] | 1000000000 |  | ~ |  |  |  | 0.13 |  | Ra ^ | 0.33333 | [6 empty] | #VALUE!
[24 empty] | h = |  | #VALUE!
[10 empty] | 1e-06 |  | ~ | 1000000000 |  | 0.36 + |  | 0.518 Ra1/4
[17 empty] | ( 1 + ( 0.559 / Pr )9/16 )4/9 | [5 empty] | Nu = |  |  | #VALUE!
[10 empty] | 1000000000 |  | ~ | 10000000000000 |  | { 0.6 + |  | 0.387 Ra1/6 |  |  |  |  | }2 |  |  |  | #VALUE!
[17 empty] | ( 1 + ( 0.559 / Pr )9/16 )8/27 | [6 empty] | h = |  | #VALUE!
NTES | [28 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## radiation
| Technical Material : | [22 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [23 empty] | Date |  |  |  | 2019. 5. 5.
[24 empty] | Revision |  |  |  | 0
[24 empty] | Sheet No. |  |  |  |  | 19 | of | 20
|  | 4. | Radiation
This is heat transfer from one body to another body, not in contact, by means of wave motion through space.
Stefan - Boltzmann Law is the fundamental equation.
|  |  |  | e | = | σ | x | T 4 |  |  |  | Where, |  |  | e |  | Energy Flux |  |  |  | Emissive Power by an Ideal Radiator ( Blackbody )
[15 empty] | σ |  | Stefan - Boltzmann Constant | [7 empty] | = | 5.6705e-08 |  |  | W/m2.K^4
[15 empty] | T |  | Temperature | [7 empty] | = | 4.8766e-08 |  |  | kcal/m2.℃^4
|  |  | Gray Body | [11 empty] | * | Blackboty is a surface or volume that absorbs all incident radiation.
Blackboty
|  |  |  | e | = | σ | x | ε | x | T 4 |  | Where, |  |  | ε |  | Surface Emissivity | [5 empty] | = | 1
[14 empty] | * | The ability to emit radiation in comparison with the ideal emission by a black body.
Rdiative Exchange between Two Surfaces
|  |  |  | Q1→2 |  | = | σ | A1 | x | F12 | x | T1^4 |  |  | Q2→1 |  | = | σ | A2 | x | F21 | x | T2^4
|  |  |  | Q |  | = | Q1→2 |  | - | Q2→1 |  |  | = | σ | A1 | x | F12 | ( | T1^4 |  | - | T2^4 |  | )
[13 empty] | = | σ | A2 | x | F21 | ( | T1^4 |  | - | T2^4 |  | )
[16 empty] | * | F is called as View Factor, Shape Factor, or Configuration Factor.
|  |  |  | Infinite Parallel Surfaces | [11 empty] | * | Total emissivity is preferred in use for engineering.
[5 empty] | F12 |  | = | 1 | / | ( | 1 | + | 1 | - | 1 | )
[11 empty] | ε1 |  | ε2
|  |  |  | One Surface enclosed by the Other | [17 empty] | if A1 is much smaller than A2,
[5 empty] | F12 |  | = | 1 | / | [ | 1 | + | A1 | ( | 1 | - | 1 | ) | ] |  | = | 1 | / | 1 |  | = | ε1
[11 empty] | ε1 |  | A2 |  | ε2 | [8 empty] | ε1
[21 empty] | * | A large enclosure such as the atmosphere
acts as a perfect absorber, black body, ε2 = 1.
Gaseous Radiation
|  |  |  | Mean Beam Length | [6 empty] | L | = | 4 | V |  |  |  | Where, |  |  | V |  | Gas Volume
[13 empty] | A | [7 empty] | A |  | Boundary Area that is irradiated
Gas Emissivity and Absorptivity
CO2 and H2O contribute to radiation of a Gas.
[5 empty] | CO2 |  |  | Emissivity |  |  | εc | depend on |  |  | : | CO2 Partial Pressure |  |  |  |  | x | Mean Beam Length |  |  |  |  | , | Gas Temperature
[8 empty] | Absorptivity |  |  | αc | additionally |  |  | : | Wall Temperature
[5 empty] | H2O |  |  | Emissivity |  |  | εw | depend on |  |  | : | H2O Partial Pressure |  |  |  |  | , | Mean Beam Length |  |  |  |  | , | Gas Temperature
[8 empty] | Absorptivity |  |  | αw | additionally |  |  | : | Wall Temperature
[5 empty] | Gas |  |  | Emissivity |  |  | εg |  |  |  | = | εc | + | εw | - | Δε
[8 empty] | Absorptivity |  |  | αg |  |  |  | = | αc | + | αw | - | Δα
Total Surface Apsorptivity
[5 empty] | αs | = |  |  |  |  | εs | [7 empty] | Where, |  |  | εs | = | Surface Emissivity
[7 empty] | ( | εs | + | αg | - | εs | x | αg | )
Radiative Heat Transfer Coeffiecient
[5 empty] | hr |  | = | σ | αs | εg | TKg^4 |  | - | αg | TKw^4
[11 empty] | Tg |  | - |  | Tw
Luminous Radiation
Later
NTES | [31 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## U
| Technical Material : | [22 empty] | Doc. No. |  |  |  | TM - HTF - 100
Heat Transfer Fundamentals | [23 empty] | Date |  |  |  | 2018. 5. 10.
[24 empty] | Revision |  |  |  | 0
[24 empty] | Sheet No. |  |  |  |  | 20 | of | 20
|  | 5. | Overall Heat Transfer Coefficient
|  |  |  | U | = | [8 empty] | 1
[6 empty] | [ | ( | 1 | + | ro | ) | 1 | + | rw | + | ( | 1 | + | ri | ) | Ao | ]
[8 empty] | ho |  |  |  | η |  |  |  |  | hi |  |  |  | Ai
MKH Unit
[5 empty] | Where, |  |  | U |  | Overall Heat Transfer Coefficient, Outside based | [11 empty] | kcal/m2.h.℃
[8 empty] | ho |  | Film Coefficient of Shell Side Fluid | [11 empty] | kcal/m2.h.℃
[8 empty] | ro |  | Fouling Resistance on Outside Surface | [11 empty] | m2.h.℃/kcal
[8 empty] | η |  | Surface Efficiency, where appicable
[8 empty] | rw |  | Resistance of Tube Wall, Outside based | [11 empty] | m2.h.℃/kcal
[8 empty] | hi |  | Film Coefficient of Tube Side Fluid | [11 empty] | kcal/m2.h.℃
[8 empty] | ri |  | Fouling Resistance on Inside Surface | [11 empty] | m2.h.℃/kcal
[8 empty] | Ao |  | Heat Transfer Surface Area, Outside | [11 empty] | m2
[8 empty] | Ai |  | Heat Transfer Surface Area, Inside | [11 empty] | m2
|  |  | Overall Heat Transfer Coefficient, Clean | [11 empty] | * | ro | = | 0 | , | ri | = | 0
|  |  |  | Uc | = | [8 empty] | 1
[6 empty] | [ | ( | 1 | + | 0 | ) | 1 | + | rw | + | ( | 1 | + | 0 | ) | Ao | ]
[8 empty] | ho |  |  |  | η |  |  |  |  | hi |  |  |  | Ai
|  |  | Cleanliness Factor | [9 empty] | If cleanliness factor is specified as requirement,
U shall be calculated as below with fouling resistances ignored.
|  |  |  | Fc | = | U | / | Uc | x | 100 |  |  | U | = | Uc | x | Fc | / | 100
|  |  | Heat Transfer Circuit | [14 empty] | Equivalent Electric Circuit
To
Tfo
|  |  |  | Heat Flow |  |  |  | Two | [10 empty] | Ro |  | Rfo |  | Rw |  | Rfi |  | Ri
|  |  |  | Q | [9 empty] | Q |  |  |  | To |  | Tfo |  | Two |  | Twi |  | Tfi |  | Ti
Twi
Tfi
Ti
[5 empty] | Outside Fluid | Fouling |  | Surface Wall |  |  | Fouling |  | Inside Fluid
|  |  |  | Q | = | U | x | ( | To | - | Ti | ) | x | Ao |  |  |  | Q | = | 1 | x | dT | = | U | x | Ao | x | dT
[5 empty] | = | ho | x | ( | To | - | Tfo | ) | x | Ao | [5 empty] | R
[5 empty] | = | 1 | x | ( | Tfo | - | Two | ) | x | Ao |  |  |  |  | Where, |  |  | R |  | Overall Resistance
[22 empty] | UAo |  | Overall Conductance | bar: U ho
[5 empty] | = | 1 | x | ( | Two | - | Twi | ) | x | Ao |  |  |  | R | = | Ro | + | Rfo | + | Rw | + | Rfi | + | Ri
[6 empty] | rw | [11 empty] | 1 |  | = | 1 |  | + | ro | + | rw | + | ri | + | 1
[5 empty] | = | 1 | x | ( | Twi | - | Tfi | ) | x | Ai |  |  |  | R: UAo; +: hoAo; Overall Conductance Rw: Ao; Overall Conductance Ri: Ai |  | hiAi
ri
[5 empty] | = | hi | x | ( | Tfi | - | Ti | ) | x | Ai |  |  |  | This equation gives same equation for " U ".
Solving simultaneous equations above results in equation for overall heat transfer coefficient, " U ".
Wall Temperature
Tube Outside Wall Temperature
|  |  |  | Two |  | = | To | - | U | x | ( | 1 | + | ro | ) | x |  |  | ( | To | - | Ti | )
ho
Tube Inside Wall Temperature
|  |  |  | Twi |  | = | Ti | - | U | x | ( | 1 | + | ri | ) | x | Ao | x | ( | Ti | - | To | )
Ai | bar: ri )
NTES | [31 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## form
| Technical Material : |  |  |  | Doc. No. | TM - HTF - 100
Heat Transfer Fundamentals |  |  |  |  | Date | 2018. 5. 10.
[5 empty] | Revision | 0
[5 empty] | Sheet No. |  | x | of | 20
|  | x. | Aaaaaa
|  |  | x.1 | Aaaaaa
NTES | [9 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## 0
| Technical Material : |  |  | Doc. No. | TM - HTF - 100
Heat Transfer Fundamentals |  |  |  | Date | 2011. 1. 5.
|  |  |  | Revision | 0
|  |  |  | Sheet No. |  | 0 | of | 20
|  | 0. | Aaaaaa
NTES | [8 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1