## cover
|  |  |  | Doc. No. |  | TM - HDF - 100 |  |  | TM - HDF - 100
Technical Guide
|  |  | Technical Material | [5 empty] | Technical Material
Hydraulic Fundamentals
sheetqty
|  |  |  | Total | 8 | sheets with a cover |  |  | 6
5
4
3
2
1 | 2019. 5. 5. | Updated. |  | S. J. Lee |  | Lee | LSJ
0 | 2008. 1. 10. | 1st Issue. |  | S. J. Lee |  | Lee | LSJ
Rev. | Date | Description |  | Prepared |  | Reviewed | Approved
나 래 열 기 술
Narai Thermal Engineering Services
| Homepage | www.ntes.co.kr |  | E-mail |  | ntes@ntes.co.kr
NTES | [7 empty] | Narai Thermal Engineering Services

## TOC
| Technical Material : |  |  | Doc. No. | TM - HDF - 100
Hydraulic Fundamentals |  |  |  | Date | 2019. 5. 5.
|  |  |  | Rev. | 0
|  |  |  | Sheet No. |  | 1 | of | 1
T a b l e of C o n t e n t s
|  | 1. | Introduction
|  | 2. | Forced Convection, Internal Flow
|  | 3. | Forced Convection, External Flow
|  | 4. | In-tube Condensation
|  | 5. | Forced Convection Boiling
NTES | [8 empty] | Narai Thermal Engineering Services

## 1
| Technical Material : |  |  |  | Doc. No. | TM - HDF - 100
Hydraulic Fundamentals |  |  |  |  | Date | 2019. 5. 5.
[5 empty] | Revision | 0
[5 empty] | Sheet No. |  | 1 | of | 6
|  | 1. | Introduction
Practical correlations for hydraulic calculations are summarized in this material.
References in english only are listed as below.
Fundamentals of Heat and Mass Transfer, 4th Edition, John Wiley & Sons
Engineering Heat Transfer, West Publishing Company
Perry's Chemical Engineers' Handbook, 7th Edition
Handbook of Heat Transfer, 3rd Edition, Mcgraw-hill
TEMA Standards, 9th Edition
Steam, its generation and use, Edition 41
NTES | [9 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## dpic
| Technical Material : | [20 empty] | Doc. No. |  |  | TM - HDF - 100
Hydraulic Fundamentals | [21 empty] | Date |  |  | 2019. 5. 5.
[22 empty] | Revision |  |  | 0 | 1
[22 empty] | Sheet No. |  |  |  | 2 | of | 6
|  | 2. | Forced Convection, Internal Flow
Physical Mechanism
[5 empty] | Velocity Boundary Layer | [15 empty] | Entrance Length
Boundary Layer
ID
[11 empty] | δ | [9 empty] | Hydraulic Entrance Length
[21 empty] | Le | ~ | 0.0565 | Red
[5 empty] | Hydraulic Entrance Length | [11 empty] | Fully developed region |  |  |  | ID
Friction Factor
|  |  |  | Laminar Flow | [5 empty] | * | Condition |  |  | : | Re | < | 2000
|  |  |  | f | = | Re
64
|  |  |  | Turbulent Flow | [5 empty] | * | Condition |  |  | : | Re | >= | 2000
Koo Equation
Smooth Tube
[5 empty] | f | = | 4 | ( | 0.0014 |  | + |  | 0.125 |  |  | )
[12 empty] | Re | ^ | 0.32
Rough Tube
[5 empty] | f | = | 4 | ( | 0.035 |  | + |  | 0.264 |  |  | )
[12 empty] | Re | ^ | 0.42
Correction Factor for Local Property Variation
Correlation by Kays-London
|  |  |  | Liquid |  |  | cf | = | ( μb / μw ) |  |  | ^ | p
|  |  |  | Vapor |  |  | cf | = | ( | Tb |  | + | 273.15 |  | ) ^ | p
[10 empty] | Tw |  | + | 273.15
[8 empty] | Where, |  |  | p Value
[14 empty] | Re | >= | 2000 |  |  | 2000 | > | Re
[13 empty] | Hot Fluid |  |  | Cold Fluid |  | Hot Fluid |  | Cold Fluid
[11 empty] | Liquid |  | -0.24 |  |  | -0.25 |  | -0.5 |  | -0.58
[11 empty] | Vapor |  | 0.1 |  |  | 0.1 |  | -1 |  | -1
Pressure Drop
|  |  |  | dP | = | f | x | L |  |  | G^2 |  |  | x | cf
[8 empty] | ID |  | 2 | g | ρ
NTES | [28 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## dpoc
| Technical Material : | [22 empty] | Doc. No. |  |  |  | TM - HDF - 100
Hydraulic Fundamentals | [23 empty] | Date |  |  |  | 2019. 5. 5.
[24 empty] | Revision |  |  |  | 0 | 1
[24 empty] | Sheet No. |  |  |  |  | 3 | of |  | 6
|  | 3. | Forced Convection, External Flow
Plain Tube Bank in Cross Flow
|  |  |  | In-line | [11 empty] | Staggered | [5 empty] | SD
OD
[25 empty] | Gmax |  | = |  | ST |  | G0
[28 empty] | ST | - | OD
[5 empty] | ST | [11 empty] | ST
|  |  |  | G0 | [11 empty] | G0 | [8 empty] | Re |  | = | Gmax |  | OD
μ
[7 empty] | SL | [11 empty] | SL
Jakob Correlation
In-line
[5 empty] | f | = | 4 [ | 0.044 |  | + | 0.08 |  | ( | SL | / | OD | ) | [6 empty] | ] | Re | ^ | -0.15
[11 empty] | ( | ST | / | OD | - | 1 | ) ^ | ( 0.43 + 1.13 ( OD / SL )
Staggered
[5 empty] | f | = | 4 [ | 0.25 |  | + | 0.118 | [8 empty] | ] | Re | ^ | -0.16
[11 empty] | ( | ST | / | OD | - | 1 | ) ^ | 1.08
Pressure Drop
[5 empty] | dP | = | f |  | Gmax |  | ^ | 2 | x | cf | x | Nr
[9 empty] | 2 | g | ρ
NTES | [32 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## _finned
| Technical Material : | [20 empty] | Doc. No. |  |  |  | TM - HDF - 100
Hydraulic Fundamentals | [21 empty] | Date |  |  |  | 2019. 5. 5.
[22 empty] | Revision |  |  |  | 0 | 1
[22 empty] | Sheet No. |  |  |  |  | 4 | of | 6
Circular Finned Tube
[17 empty] | Area Calculation |  |  |  |  | * | in | m2 | [6 empty] | Area
t
Area per 1 m Tube, Tube Inside
[9 empty] | ID |  | OD |  | Df |  |  |  | ai | = | π | x | ID | / | 1000
Area per 1 m Tube, Tube Outside, Bare
[17 empty] | ab | = | π | x | OD | / | 1000
[11 empty] | Hf | [5 empty] | Area per 1 m Tube, Fin
|  |  | tf |  |  | Pf | [10 empty] | af | = | [ π / 4 x |  |  | 2 x ( | Df | ^2 | - | OD | ^2 | )
[19 empty] | + | π | x |  | Df | x |  | tf | ] x | FPM | / 10^6
|  |  | Where, |  | OD |  | Tube OD | [9 empty] | Area per 1 m Tube, Tube Outside, Unfinned Surface
[5 empty] | t |  | Tube Thickness |  |  |  |  | ID |  | Tube ID |  |  | ar | = | π | x | OD | x ( | 1000 |  | - | tf | x | FPM | ) /10^6
[5 empty] | Hf |  | Fin Height |  |  |  |  | tf |  | Fin Thick |  |  | Area per 1 m Tube, Tube Outside
[5 empty] | Df |  | Fin OD |  |  |  |  | Pf |  | Fin Pitch |  |  | ao |  | = | af | + | ar
[5 empty] | FPI |  | Fin Q'ty per Inch | [9 empty] | Ratio of Area, Outside / Inside
[5 empty] | FPM |  | Fin Q'ty per Meter |  |  |  |  | * | in | mm |  |  | Raoi |  | = | ao | / | ai
Ratio of Area, Outside, Finned / Bare
[17 empty] | Raob |  | = | ao | / | ab
Tube Arrangement
|  |  |  | In-line | [8 empty] | Staggered
SD
[21 empty] | Gmax |  | = |  | ST |  | G0
[24 empty] | ST | - | OD
[5 empty] | ST | [8 empty] | ST
|  |  |  | G0 | [8 empty] | G0 | [7 empty] | Re |  | = | Gmax |  | OD
μ
[7 empty] | SL | [8 empty] | SL
|  |  | Briggs and Young Correlation | [7 empty] | * | for | Staggered
|  |  |  | f | = | 37.86 |  | Re | ^ | -0.316 |  | ( | ST |  | ) ^ | -0.927 | ( | ST |  | ) ^ | 0.515
[13 empty] | OD |  |  |  |  | SD
Pressure Drop
|  |  |  | dP | = | f |  | Gmax |  | ^ | 2 | x | cf | x | Nr
[8 empty] | 2 | g | ρ
NTES | [29 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## dpcd
| Technical Material : |  |  | Doc. No. | TM - HDF - 100
Hydraulic Fundamentals |  |  |  | Date | 2019. 5. 5.
|  |  |  | Revision | 0 | 1
|  |  |  | Sheet No. |  | 5 | of | 6
|  | 4. | In-tube Condensation
Later
NTES | [8 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## dpboil
| Technical Material : | [22 empty] | Doc. No. |  |  |  | TM - HDF - 100
Hydraulic Fundamentals | [23 empty] | Date |  |  |  | 2019. 5. 5.
[24 empty] | Revision |  |  |  | 0 | 1
[24 empty] | Sheet No. |  |  |  |  | 6 | of |  | 6
|  | 5. | Forced Convection Boiling
Friction Loss
|  |  |  | ΔPftp |  | = | Φ | ^ | 2 | x | ΔPfl
[6 empty] | Where, |  |  | Φ | = | [ | 1 | + | 21 | + | ( | 1 | ) ^ | 2 | ] ^ | 0.5
[14 empty] | X |  |  | X
[10 empty] | Where, |  |  | X |  | Martinelli Parameter
[9 empty] | ΔPfl |  | Friction Loss based on Liquid Properties
Acceleration Loss
|  |  |  | ΔPatp |  | = | [ | 1 | ( | Gl | ^ | 2 | + | Gv | ^ | 2 | ) ] |  | - | [ | 1 | ( | Gl | ^ | 2 | + | Gv | ^ | 2 | ) ]
[8 empty] | g |  | Rl |  | ρl |  | Rv |  | ρv |  | out |  |  | gc |  | Rl |  | ρl |  | Rv |  | ρv |  | inlet
Static Head Loss
|  |  |  | ΔPstp |  | = | ρm | x | ΔH
[6 empty] | Where, |  |  | Mean Density |  |  |  | ρm | = |  |  |  | ρl |  |  |  | ln( | ρl | )
[15 empty] | ( | ρl | / | ρv | - | 1 | ) |  | ρv
[9 empty] | ΔH |  | Hight Difference
Contraction and Expansion
Contraction
[5 empty] | Kc |  | = | 1.2 | ( | 1 | - | Rv | ) | [ | 1 | - | ( | A2 | ) ^ | 2 | ]
A1
[5 empty] | ΔPctp |  | = | Kc |  | Gt2 | ^ | 2
[10 empty] | 2 | g | ρl
Expansion
[5 empty] | Ke |  | = | -2 | [ | ( | 1 | - | x | ) ^ | 2 | + | x^2 | ρl | ] [ | A1 | - | ( | A1 | ) ^ | 2 | ]
[10 empty] | Rl | [6 empty] | Rv | ρv |  | A2 |  |  | A2
[5 empty] | ΔPetp |  | = | Ke |  | Gt1 | ^ | 2
[10 empty] | 2 | g | ρl
[29 empty] | 1 |  | 2
[28 empty] | Flow Area | A1 |  | A2
NTES | [32 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## form
| Technical Material : |  |  |  | Doc. No. | TM - HDF - 100
Hydraulic Fundamentals |  |  |  |  | Date | 2018. 5. 10.
[5 empty] | Revision | 0
[5 empty] | Sheet No. |  | x | of | 6
|  | x. | Aaaaaa
|  |  | x.1 | Aaaaaa
NTES | [9 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1

## 0
| Technical Material : |  |  | Doc. No. | TM - HDF - 100
Hydraulic Fundamentals |  |  |  | Date | 2011. 1. 5.
|  |  |  | Revision | 0
|  |  |  | Sheet No. |  | 0 | of | 6
|  | 0. | Aaaaaa
NTES | [8 empty] | Narai Thermal Engineering Services
Note on AJ4: Cell is filled !
1