## cover
|  |  |  | Doc. No. |  | TM - PCSC - 100 |  |  | TM - PCSC - 100
Technical Guide
|  |  | Technical Material | [5 empty] | Technical Material
Process Calculations in Steam Cycle
sheetqty
|  |  |  | Total | 14 | sheets with a cover |  |  | 12
5
4
3
2
1 | 2018. 3. 10. | Updated. |  | S. J. Lee |  | Lee | LSJ
0 | 2005. 1. 10. | 1st Issue. |  | S. J. Lee |  | Lee | LSJ
Rev. | Date | Description |  | Prepared |  | Reviewed | Approved
나 래 열 기 술
Narai Thermal Engineering Services
| Homepage | www.ntes.co.kr |  | E-mail |  | ntes@ntes.co.kr
NTES | [7 empty] | Narai Thermal Engineering Services

## TOC
| Technical Material : |  |  |  | Doc. No. | TM - PCSC - 100
Process Calculations in Steam Cycle |  |  |  |  | Date | 2018. 3. 10.
[5 empty] | Rev. | 0
[5 empty] | Sheet No. |  | 1 | of | 1
T a b l e of C o n t e n t s
|  | 1. |  | Temperaure - Enthalpy Diagram ( T - h Diagram )
|  | 2. |  | Heat and Mass Balance in Equipments
|  |  | 2.1 | Steam Surface Condenser
|  |  | 2.2 | LP Feedwater Heater
|  |  | 2.3 | Deaerator
|  |  | 2.4 | HP Feedwater Heater
|  |  | 2.5 | Heat Recovery Steam Generator ( HRSG )
|  | 3. |  | Steam Drum
|  |  | 3.1 | Evaporation
|  |  | 3.2 | Blowdown
|  | 4. |  | Flash Tank
|  | 5. |  | Blowdown Tank
|  | 6. |  | De-superheater
|  | 7. |  | Steam Pressure Reducing
NTES | [9 empty] | Narai Thermal Engineering Services

## 1
| Technical Material : | [18 empty] | Doc. No. |  |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [19 empty] | Date |  |  | 2018. 3. 10.
[20 empty] | Rev. |  |  | 0
[20 empty] | Sheet No. |  |  |  | 1 | of | 12
|  | 1. | Temperaure - Enthalpy Diagram ( T - h Diagram )
A phase diagram is a type of chart to show conditions ( pressure, temperaure, volume, etc. ).
T - h Diagram for water and steam is effectively used for process calculations in steam cycle.
T - h Diagram
T
|  |  |  | Temp. |  | ℃
|  |  | 300 | [18 empty] | Pressure
[22 empty] | 20 | kg/cm2.g
[11 empty] | Sat. Water Line | [6 empty] | Sat. Steam Line
Wet Steam
[7 empty] | Sub-cooled Water | [7 empty] | ( Mixture of Water and Steam ) | [7 empty] | Superheated Steam
|  |  | #VALUE! | [9 empty] | Evaporation Line | [6 empty] | Constant Pressure Line
[12 empty] | x |  |  | x
[12 empty] | 0.1 |  |  | 0.9
80
h
[10 empty] | hL |  | hx |  |  | hx |  |  | hV |  |  |  |  | Enthalpy
[6 empty] | #VALUE! |  |  |  | #VALUE! |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  | kcal/kg
[13 empty] | Latent Heat | = | hV | - | hL
[14 empty] | = | #VALUE!
Steam Quality
[5 empty] | x | = | Mass of Vapor |  |  |  | = | mV |  |  | Where, |  | mV |  | Mass of Vapor
[7 empty] | Total Mass |  |  |  |  | m |  |  |  |  | m |  | Total Mass
[17 empty] | mL |  | Mass of Liquid |  |  | = | m | - | mV
[5 empty] | hx | = | ( | 1 | - | x | ) | hL | + | x | hV | = | hL | + | x | ( | hV | - | hL | )
Water and steam properties are calculated in accordance with :
IAPWS Industrial Formulation 1977 for the Thermodynamic Properties of Water and Steam ( IAPWS - IF97 )
NTES | [26 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1

## SSC
| Technical Material : | [15 empty] | Doc. No. |  |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [16 empty] | Date |  |  | 2018. 3. 10.
[17 empty] | Rev. |  |  | 0
[17 empty] | Sheet No. |  |  |  | 2 | of | 12
|  | 2. | Heat and Mass Balance in Equipments
|  |  | 2.1 | Steam Surface Condenser
T - h Diagram
T
|  |  |  | Temp. |  | ℃
Exhaust Steam
[12 empty] | 0.1 | #VALUE!
|  |  | #VALUE! | [8 empty] | #VALUE! | bar.g
xi
0.9
TTD
[17 empty] | h |  |  | #VALUE!
[9 empty] | hL |  |  |  | hxi |  | hV |  | Enthalpy |  |  | #VALUE!
[9 empty] | #VALUE! |  |  |  | #VALUE! |  | #VALUE! |  | kcal/kg
Condensing Zone
40
|  |  | 32 | [11 empty] | Cooling Water |  |  |  | TTD as per HEI 4.1.2
[15 empty] | Pressure |  |  |  | Recommended Min.
[15 empty] | 3 | bar.g |  |  | 2.7778 |  | ℃
[9 empty] | hcwi |  |  |  | hcwo
[9 empty] | #VALUE! |  |  |  | #VALUE!
Calculation
Heat Change of Exhaust Steam
[5 empty] | Hs |  | = | ms |  | x | ( | hxi | - | hL |  | )
[7 empty] | = | 100000 |  | x | ( | #VALUE! | - | #VALUE! |  | ) | = | #VALUE! |  |  |  | kcal/h
[17 empty] | = | #VALUE! |  |  |  | kW
Required Flowrate of Cooling Water
[5 empty] | mcw |  | = | Hs |  | / | ( | hcwo | - | hcwi |  | )
[7 empty] | = | #VALUE! |  | / | ( | #VALUE! | - | #VALUE! |  | ) | = | #VALUE! |  |  |  | kg/h
|  |  |  | * | Additional flows such as Gland Steam, Heater Drain, etc. should be included in above.
NTES | [23 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1

## LP
| Technical Material : | [17 empty] | Doc. No. |  |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [18 empty] | Date |  |  | 2018. 3. 10.
[19 empty] | Rev. |  |  | 0
[19 empty] | Sheet No. |  |  |  | 3 | of | 12
|  |  | 2.2 | LP Feedwater Heater
T - h Diagram
T
|  |  |  | Temp. |  | ℃
Extract Steam
|  |  | 200 | [16 empty] | Pressure
[20 empty] | 3 | bar.g
#VALUE!
110
h
[6 empty] | ho |  |  |  | hL | [6 empty] | hV |  | hi |  | Enthalpy
[6 empty] | #VALUE! |  |  |  | #VALUE! | [6 empty] | #VALUE! |  | #VALUE! |  | kcal/kg
TTD
[7 empty] | Drain Subcooling Zone | [6 empty] | Condensing Zone | [8 empty] | #VALUE!
[7 empty] | ( | DC | ) | [13 empty] | #VALUE!
| DCA |  | 135
10
| OK ! |  | #VALUE! | [18 empty] | TTD as per HEI 2.3
[13 empty] | LP Feedwater | [8 empty] | Recommended Min.
|  |  | 100 | [9 empty] | Pressure |  |  | Flowrate | [5 empty] | 1.1111 |  | ℃
[13 empty] | 10 | bar.g |  | 200000 |  | kg/h |  |  |  | for " without DSH "
DCA as per HEI 2.4
Recommended Min. | [5 empty] | hfwi |  |  |  | hdco | [8 empty] | hfwo
5.5556 |  | ℃ |  |  |  | #VALUE! |  |  |  | #VALUE! | [8 empty] | #VALUE!
for ' Integral DC '
Formulation and Calculation
Heat Change of LP Feedwater
[5 empty] | Hfw |  | = | mfw |  |  | x | ( | hfwo |  | - | hfwi |  | ) | -> | #VALUE! |  |  |  | kW
[7 empty] | = | 200000 |  |  | x | ( | #VALUE! |  | - | #VALUE! |  | ) | = | #VALUE! |  |  |  | kcal/h
Required Flowrate of Extract Steam
[5 empty] | ms |  | = | Hfw |  |  | / | ( | hi |  | - | ho |  | )
[7 empty] | = | #VALUE! |  |  | / | ( | #VALUE! |  | - | #VALUE! |  | ) | = | #VALUE! |  |  |  | kg/h
Heat Change of Drain Subcooling Zone
[5 empty] | Hdc |  | = | ms |  |  | x | ( | hL |  | - | ho |  | )
[7 empty] | = | #VALUE! |  |  | x | ( | #VALUE! |  | - | #VALUE! |  | ) | = | #VALUE! |  |  |  | kcal/h
Ehtalpy of LP Feedwater at DC Outlet
[5 empty] | hdco |  | = | hfwi + Hdc / mfw | [10 empty] | = | #VALUE! |  |  |  | kcal/kg
Temperature of LP Feedwater at DC Outlet
[5 empty] | Tfwdco |  | = | Backward Equation, T( p, h ) | [10 empty] | = | #VALUE! |  |  |  | ℃
|  |  |  | * | Drain from another heater, if any, should be included in above.
NTES | [25 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1

## DEA
| Technical Material : | [17 empty] | Doc. No. |  |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [18 empty] | Date |  |  | 2018. 3. 10.
[19 empty] | Rev. |  |  | 0
[19 empty] | Sheet No. |  |  |  | 4 | of | 12
|  | 2.3 | Deaerator
Schematic Diagram
Condensate
[10 empty] | 1 |  | 80 | [8 empty] | Legend
[10 empty] | 100000 |  | #VALUE! |  |  | Pv | 1 | % of Heating Steam |  |  |  | P | T
|  |  |  | Make-up Water | [5 empty] | mc |  | hc |  |  |  | Vent Steam |  |  |  |  | m | h
|  |  |  | 1 |  | 20 | [9 empty] | 1 |  | #VALUE! |  |  | P | Pressure |  |  | bar.g
|  |  |  | 5000 |  | #VALUE! | [9 empty] | #VALUE! |  | #VALUE! |  |  | T | Temperature |  |  | ℃
|  |  |  | mk |  | hk | [9 empty] | mv |  | hv |  |  | m | Flowrate |  |  | kg/h
[21 empty] | h | Enthalpy |  |  | kcal/kg
|  |  | S/H | Heating Steam | [11 empty] | HT Condensate |  |  |  | Tsat.
|  |  |  | 3 |  | 180 |  |  |  | OP | 1 |  | bar.g |  |  | 5 |  | 150 |  | #VALUE!
|  |  |  | #VALUE! |  | #VALUE! |  |  |  | OT | #VALUE! |  | ℃ |  |  | 10000 |  | #VALUE!
|  |  |  | ms |  | hs | [9 empty] | mh |  | hh
[5 empty] | Tsat. > | #VALUE!
[5 empty] | Ts/h > | 180
Feedwater
[10 empty] | 1 |  | #VALUE!
[10 empty] | #VALUE! |  | #VALUE!
[10 empty] | mf |  | hf
Formulation and Calculation
|  |  |  | mc |  | + | mk |  | + | mh |  | + | ms |  | = | mf |  | + | mv |  | <- | Mass Conservation Law
|  |  |  | mc | hc | + | mk | hk | + | mh | hh | + | ms | hs | = | mf | hf | + | mv | hv | <- | Energy Conservation Law
[16 empty] | ↓ |  |  | ↓
[16 empty] | mc + mk + mh + ms ( 1 - Pv / 100 ) |  |  | ms x Pv / 100
|  |  | -> | ms | hs | - | ms x Pv / 100 |  |  | x | hv | - | ms ( 1 - Pv / 100 ) |  |  |  | x | hf
[15 empty] | = | mc x ( hf - hc ) + mk x ( hf - hk ) + mh x ( hf - hh )
|  |  | -> | ms | = | mc x ( hf - hc ) + mk x ( hf - hk ) + mh x ( hf - hh ) | [14 empty] | = | #VALUE! |  |  | kg/h
[6 empty] | ( | hs - Pv /100 x hv - ( 1 - Pv / 100 ) x hf | [9 empty] | )
|  |  |  | mv | = | ms | x | Pv | / | 100 | = | #VALUE! |  | x | 1 | / | 100 |  |  |  | = | #VALUE! |  |  | kg/h
|  |  |  | mf | = | mc | + | mk | + | mh | + | ms | - | mv | [6 empty] | = | #VALUE! |  |  | kg/h
Heat & Mass Balance
|  |  |  | Incoming Fluids |  |  |  |  | Flowrate |  |  |  | Enthalpy |  |  | Energy
|  |  |  | Condensate |  |  |  |  | 100000 |  |  | x | #VALUE! |  | = | #VALUE!
|  |  |  | Make-up Water |  |  |  |  | 5000 |  |  | x | #VALUE! |  | = | #VALUE!
|  |  |  | HT Condensate |  |  |  |  | 10000 |  |  | x | #VALUE! |  | = | #VALUE!
|  |  |  | Heating Steam |  |  |  |  | #VALUE! |  |  | x | #VALUE! |  | = | #VALUE!
|  |  |  | Outgoing Fluids |  |  |  | Sum > | #VALUE! | [5 empty] | Sum > | #VALUE!
|  |  |  | Feedwater |  |  |  |  | #VALUE! |  |  | x | #VALUE! |  | = | #VALUE!
|  |  |  | Vent Steam |  |  |  |  | #VALUE! |  |  | x | #VALUE! |  | = | #VALUE!
[8 empty] | Sum > | #VALUE! | [5 empty] | Sum > | #VALUE!
[8 empty] | Dev. > | #VALUE! |  |  | % |  |  |  | #VALUE! |  |  |  | %
NTES | [25 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1

## HP
| Technical Material : | [17 empty] | Doc. No. |  |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [18 empty] | Date |  |  | 2018. 3. 10.
[19 empty] | Rev. |  |  | 0
[19 empty] | Sheet No. |  |  |  | 5 | of | 12
|  |  | 2.4 | HP Feedwater Heater
T - h Diagram
|  |  |  | T |  | Temp. |  | ℃ | [11 empty] | Extract Steam
|  |  | 300 | [16 empty] | Pressure
[20 empty] | 31 | bar.g
|  |  | #VALUE! | [7 empty] | Ideal Process without ΔP in DSH
|  |  | #VALUE! | [7 empty] | Real Process with ΔP in DSH | [6 empty] | Pressure |  | ΔP in DSH
[18 empty] | 30 | bar.g | 1 | #VALUE!
210
h
[6 empty] | ho |  |  | hL | hLid |  |  |  |  | hV |  | hVid |  | hi |  | Enthalpy
[6 empty] | #VALUE! |  |  | #VALUE! | #VALUE! |  |  |  |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | kcal/kg
TTD
[7 empty] | Drain Subcooling Zone | [5 empty] | Condensing Zone |  |  |  | Desuperheating Zone | [5 empty] | #VALUE!
[7 empty] | ( | DC | ) | [7 empty] | ( | DSH | ) |  |  |  | #VALUE!
235
| DCA |  | #VALUE! | [18 empty] | TTD as per HEI 2.3
| 10 | [20 empty] | Recommended Max.
| OK ! |  | #VALUE! | [18 empty] | 1.1111 |  | ℃
[11 empty] | HP Feedwater | [10 empty] | for ' with DSH '
|  |  | 200 | [7 empty] | Pressure |  |  | Flowrate
[11 empty] | 100 | bar.g |  | 200000 |  | kg/h
DCA as per HEI 2.4
Recommended Min. | [5 empty] | hfwi |  |  | hdco | [6 empty] | hdsi |  |  | hfwo
5.5556 |  | ℃ |  |  |  | #VALUE! |  |  | #VALUE! | [6 empty] | #VALUE! |  |  | #VALUE!
for ' Integral DC '
Formulation and Calculation
Heat Change of HP Feedwater
[5 empty] | Hfw |  | = | mfw |  | x | ( | hfwo |  | - | hfwi |  | ) |  | -> | #VALUE! |  |  |  | kW
[7 empty] | = | 200000 |  | x | ( | #VALUE! |  | - | #VALUE! |  | ) |  | = | #VALUE! |  |  |  | kcal/h
Required Flowrate of Extract Steam
[5 empty] | ms |  | = | Hfw |  | / | ( | hi |  | - | ho |  | )
[7 empty] | = | #VALUE! |  | / | ( | #VALUE! |  | - | #VALUE! |  | ) |  | = | #VALUE! |  |  |  | kg/h
Heat Change of Drain Subcooling Zone
[5 empty] | Hdc |  | = | ms |  | x | ( | hL |  | - | ho |  | )
[7 empty] | = | #VALUE! |  | x | ( | #VALUE! |  | - | #VALUE! |  | ) |  | = | #VALUE! |  |  |  | kcal/h
Ehtalpy of HP Feedwater at DC Outlet
[5 empty] | hdco |  | = | hfwi + Hdc / mfw | [10 empty] | = | #VALUE! |  |  |  | kcal/kg
Heat Change of Desuperheating Zone
[5 empty] | Hds |  | = | ms |  | x | ( | hi |  | - | hV |  | )
[7 empty] | = | #VALUE! |  | x | ( | #VALUE! |  | - | #VALUE! |  | ) |  | = | #VALUE! |  |  |  | kcal/h
Ehtalpy of HP Feedwater at DSH Inlet
[5 empty] | hdsi |  | = | hfwo - Hds / mfw | [10 empty] | = | #VALUE! |  |  |  | kcal/kg
|  |  |  | * | Drain from another heater, if any, should be included in above.
NTES | [25 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1

## HRSG
| Technical Material : | [16 empty] | Doc. No. |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [17 empty] | Date |  | 2018. 3. 10.
[18 empty] | Rev. |  | 0
[18 empty] | Sheet No. |  |  | 6 | of | 12
|  | 2.5 | Heat Recovery Steam Generator ( HRSG )
T - h Diagram
T
|  |  | Temp. |  | ℃
Output Steam
|  | 300 | [16 empty] | Pressure
[19 empty] | 19.5 | bar.g
[13 empty] | EV Pressure | [5 empty] | ms
|  | #VALUE! | [10 empty] | 20 |  | bar.g |  |  |  | 20000 | kg/h
Kind
|  | 150 | [16 empty] | S/H
120
h
[5 empty] | hfw |  |  | heco |  | hL | [5 empty] | hV |  | hs |  | Enthalpy
[5 empty] | #VALUE! |  |  | #VALUE! |  | #VALUE! | [5 empty] | #VALUE! |  | #VALUE! |  | kcal/kg
[6 empty] | Economizer | [5 empty] | Evaporator |  |  |  |  | Superheater
[11 empty] | Blowdown | 3 |  | % Steam Flow
[6 empty] | mfw | [5 empty] | mbd |  |  |  |  | msh
[5 empty] | Flowrate > | 20600 | [5 empty] | 600 |  |  |  |  | 20000
Calculation
Heat Change in Economizer
|  |  |  | Heco |  | = | mfw |  |  | x | ( | heco |  | - | hfw |  | )
[6 empty] | = | 20600 |  |  | x | ( | #VALUE! |  | - | #VALUE! |  | ) | = | #VALUE! |  |  | kcal/h
Heat Change in Evaporator
|  |  |  | Hev |  | = | ms |  |  | x | ( | hV |  | - | heco |  | )
[7 empty] | 20000 |  |  | x | ( | #VALUE! |  | - | #VALUE! |  | )
[6 empty] | + | mbd |  |  | x | ( | hL |  | - | heco |  | )
[7 empty] | 600 |  |  | x | ( | #VALUE! |  | - | #VALUE! |  | ) | = | #VALUE! |  |  | kcal/h
Heat Change in Superheater
|  |  |  | Hsh |  | = | msh |  |  | x | ( | hs |  | - | hV |  | )
[6 empty] | = | 20000 |  |  | x | ( | #VALUE! |  | - | #VALUE! |  | ) | = | #VALUE! |  |  | kcal/h
Capacity of Heat Recovery Steam Generator ( HRSG )
|  |  |  | H |  | = | Heco |  | + | Hev |  | + | Hsh |  |  |  |  | = | #VALUE! |  |  | kcal/h
[18 empty] | = | #VALUE! |  |  | kW
NTES | [23 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1

## SD
| Technical Material : | [18 empty] | Doc. No. |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [19 empty] | Date |  | 2018. 3. 10.
[20 empty] | Rev. |  | 0
[20 empty] | Sheet No. |  |  | 7 | of | 12
|  | 3. | Steam Drum
|  |  | 3.1 | Evaporation
Schematic Diagram
[17 empty] | Steam |  |  |  | Legend
[17 empty] | 20 |  | #VALUE! |  | P | T |  |  |  |  | Heat Balance
[17 empty] | #VALUE! |  | #VALUE! |  | m | h |  |  |  |  | Hs | = | ms |  | x | hs | = | #VALUE! |  | x | #VALUE!
[17 empty] | ms |  |  |  | P | Pressure |  |  | bar.g |  |  | = | #VALUE! |  | kcal/h
[21 empty] | T | Temperature |  |  | ℃ |  | Hfw | = | mfw |  | x | hfw | = | #VALUE! |  | x | #VALUE!
[12 empty] | Steam Drum | [8 empty] | m | Flowrate |  |  | kg/h |  |  | = | #VALUE! |  | kcal/h
[11 empty] | OP | 20 |  | bar.g | [6 empty] | h | Enthalpy |  |  | kcal/kg |  | Hbd | = | mbd |  | x | hbw | = | #VALUE! |  | x | #VALUE!
[11 empty] | OT | #VALUE! |  | ℃ | [13 empty] | = | #VALUE! |  | kcal/h
[5 empty] | Feedwater | [6 empty] | Enthalpy | [5 empty] | 20 |  | #VALUE! | [6 empty] | Heat added to Steam Drum
[5 empty] | 20 |  | 120 |  |  |  | Steam | hs | #VALUE! |  |  |  |  | 122750 |  | #VALUE! | [6 empty] | Ha | = | Hs |  | + | Hbd |  | - | Hfw
[5 empty] | #VALUE! |  | #VALUE! |  |  |  | BW | hbw | #VALUE! |  |  |  | Steam | 12275 |  | mis | [7 empty] | = | #VALUE! |  | + | #VALUE! |  | - | #VALUE!
[5 empty] | mfw |  | hfw | [9 empty] | Water | 110475 |  | =mbw - mis | [7 empty] | = | #VALUE! |  | kcal/h
[17 empty] | Steam Quality | 0.1
[5 empty] | Blowdown | [21 empty] | Heat from Heat Recovery Unit
[5 empty] | 20 |  | #VALUE! | [5 empty] | 20 |  | #VALUE! | [11 empty] | Hr | = | mbw |  | x | ( | his | - | hbw | )
[5 empty] | #VALUE! |  | #VALUE! | [5 empty] | 122750 |  | #VALUE! | [12 empty] | = | 122750 |  | x | ( | #VALUE! | - | #VALUE! | )
[5 empty] | mbd |  | = hbw | [5 empty] | mbw |  | = hbw | [12 empty] | = | #VALUE! |  | kcal/h
|  |  |  | Design Blowdown Rate | [8 empty] | Circulation Ratio | [8 empty] | Evaporator |  |  |  |  | #VALUE! | %FW Flow
|  |  |  | Rd | 2.91 |  | %FW Flow | [5 empty] | 10 | [13 empty] | #VALUE! | %Steam Flow |  | #VALUE!
Formulation and Calculation
Mass Balance
[5 empty] | mfw | - | mbd |  |  |  | = | ms
|  |  |  | -> | mfw | - | Rd / 100 x mfw |  |  |  | = | ms
|  |  |  | -> | mfw |  | = | ms / ( 1 - Rd / 100 )
|  |  |  | -> | mbd |  | = | mfw | - | ms | = | ms x Rd / 100 / ( 1 - Rd / 100 )
Heat Balance
[5 empty] | ms x hs |  | = | mis x hs |  | + | ( mbw - mis ) x hbw |  |  |  | - | mbw x hbw |  |  | + | mfw x hfw |  | - | mbd x hbw
[7 empty] | = | mis x hs |  | - | mis x hbw |  |  | + | ms / ( 1 - Rd / 100 ) x hfw
[14 empty] | - | ms x Rd / 100 / ( 1 - Rd / 100 ) x hbw
|  |  |  | -> | ms |  | = | mis x ( hs - hbw ) | [13 empty] | = | #VALUE! |  | kg/h
[8 empty] | ( | hs - hfw / ( 1 - Rd / 100 ) + hbw x Rd / 100 / ( 1 - Rd / 100 ) | [11 empty] | )
NTES | [25 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1

## blowdown
| Technical Material : | [17 empty] | Doc. No. |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [18 empty] | Date |  | 2018. 3. 10.
[19 empty] | Rev. |  | 0
[19 empty] | Sheet No. |  |  | 8 | of | 12
|  | 3.2 | Blowdown
Schematic Diagram
[16 empty] | Steam Out |  |  |  | Legend
[16 empty] | 20 |  | #VALUE! |  | P | T |  |  |  |  | Heat Balance
[15 empty] | ms | 10000 |  | #VALUE! |  | m | h |  |  |  |  | Hs | = | ms |  | x | hs | = | 10000 |  | x | #VALUE!
[15 empty] | S | 1 |  |  |  | P | Pressure |  |  | bar.g |  |  | = | #VALUE! |  | kcal/h
[20 empty] | T | Temperature |  |  | ℃ |  | Hfw | = | mfw |  | x | hfw | = | 10300 |  | x | #VALUE!
[11 empty] | Steam Drum | [8 empty] | m | Flowrate |  |  | kg/h |  |  | = | #VALUE! |  | kcal/h
[10 empty] | OP | 20 |  | bar.g | [6 empty] | h | Enthalpy |  |  | kcal/kg |  | Hbd | = | mbd |  | x | hbd | = | 300 |  | x | #VALUE!
[10 empty] | OT | #VALUE! |  | ℃ | [6 empty] | F,B,S | TDS |  |  | ppm, mg/kg |  |  | = | #VALUE! |  | kcal/h
|  |  |  | Feedwater | [21 empty] | Heat added to Steam Drum
|  |  |  | 20 |  | 120 |  |  |  | Oper. TDS in BW | [15 empty] | Ha | = | Hs |  | + | Hbd |  | - | Hfw
|  |  | mfw | 10300 |  | #VALUE! |  |  |  | B | 1000 | [15 empty] | = | #VALUE! |  | + | #VALUE! |  | - | #VALUE!
|  |  | F | 10 | [22 empty] | = | #VALUE! |  | kcal/h
|  |  | mfw | = | ms + mbd | [10 empty] | Blowdown | [9 empty] | 3 | %Steam Flow
|  |  |  | = | ms ( 1 + Rd / 100 ) | [10 empty] | 20 |  | #VALUE! |  | Design Blowdown Rate | [5 empty] | 2.9126 | %FW Flow |  | 300
[15 empty] | mbd | 300 |  | #VALUE! |  | Rd | 3 |  | %Steam Flow
[15 empty] | B | 1000
[15 empty] | mbd | = | ms x Rd / 100
Formulation and Calculation
|  |  |  | Blowdown Rate in Operation | [6 empty] | * based on given TDS.
|  |  |  | mfw x F |  |  |  |  | = | ms x S |  | + | mbd x B
|  |  | -> | ms ( 1 + Ro / 100 ) x F |  |  |  |  | = | ms x S |  | + | ms x Ro / 100 x B
|  |  | -> | ( 1 + Ro / 100 ) x F |  |  |  |  | = | S |  | + | Ro / 100 x B
|  |  | -> | Ro / 100 x F |  |  | - | Ro / 100 x B |  |  | = | S | - | F
|  |  | -> | Ro | = | 100 | ( | F | - | S | ) | = | 100 | ( | 10 | - | 1 | ) | = | 0.90909 |  |  | %Steam Flow
[7 empty] | ( | B | - | F | ) |  |  | ( | 1000 | - | 10 | )
[19 empty] | -> | 90.9091 |  |  | kg/h
|  |  |  | Maxumum Allowable TDS in Feedwater | [8 empty] | * based on given Design Blowdown Rate
|  |  | -> | Fm x ( Rd + 100 ) |  |  |  | = | S x 100 + Rd x B
|  |  | -> | Fm | = | ( S x 100 + Rd x B ) / ( Rd + 100 ) | [12 empty] | = | 30.0971 |  |  | ppm, mg/kg
NTES | [24 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1

## FTK
| Technical Material : | [18 empty] | Doc. No. |  |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [19 empty] | Date |  |  | 2018. 3. 10.
[20 empty] | Rev. |  |  | 0
[20 empty] | Sheet No. |  |  |  | 9 | of | 12
|  | 4. | Flash Tank
Schematic Diagram
Flash Steam
[12 empty] | 5 |  | #VALUE!
[12 empty] | #VALUE! |  | #VALUE!
[12 empty] | mV |  | hV
|  |  |  | Blowdown Water | [16 empty] | Legend
|  |  |  | 20 |  | #VALUE! | [14 empty] | P | T
|  |  |  | 1000 |  | #VALUE! | [5 empty] | OP | 5 |  | bar.g | [5 empty] | m | h
|  |  |  | mi |  | hi | [5 empty] | OT | #VALUE! |  | ℃ | [5 empty] | P | Pressure |  |  | bar.g |  |  | bar.g |  | < Press. Unit |  | 대기압
[21 empty] | T | Temperature |  |  | ℃ |  |  | Gauge |  | < Gauge or Absolute |  | 0
[12 empty] | Condensate | [8 empty] | m | Flowrate |  |  | kg/h |  |  |  |  | < Temp.
[12 empty] | 5 |  | #VALUE! | [6 empty] | h | Enthalpy |  |  | kcal/kg
[12 empty] | #VALUE! |  | #VALUE! | [13 empty] | H&M Balance
[12 empty] | mL |  | hL | [13 empty] | m | 1000 |  | #VALUE! | #VALUE!
|  |  | T - h Diagram | [25 empty] | hi |  | hV | hL
[28 empty] | h | #VALUE! |  | #VALUE! | #VALUE! | Dev.
|  |  | T |  | Temp. |  | ℃ | [20 empty] | mxh | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | %
|  | #VALUE! | [16 empty] | Pressure
[19 empty] | 20 | bar.g
|  | #VALUE! | [16 empty] | Pressure
[19 empty] | 5 | bar.g
h
[6 empty] | hL |  |  |  | hi |  |  |  |  | hV | [6 empty] | Enthalpy
[6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! | [6 empty] | kcal/kg
Formulation and Calculation
|  |  |  | Flowrate of Flash Steam | [5 empty] | * | A | -> | B
|  |  |  | mi |  | = | mV |  | + | mL | [10 empty] | <- | Mass Conservation Law
|  |  |  | mi | hi | = | mV | hV | + | mL | hL | = | mV | hV | + ( | mi | - | mV | ) | hL | <- | Energy Conservation Law
|  |  | -> | mV | = | mi | ( | hi | - | hL | ) | = | 1000 |  | ( | #VALUE! |  | - | #VALUE! |  | ) |  | = | #VALUE! |  | kg/h
[7 empty] | ( | hV | - | hL | ) |  |  |  | ( | #VALUE! |  | - | #VALUE! |  | )
Steam Quality
|  |  |  | x | = |  | ( | hi | - | hL | ) | = |  |  | ( | #VALUE! |  | - | #VALUE! |  | ) |  | = | #VALUE!
[7 empty] | ( | hV | - | hL | ) |  |  |  | ( | #VALUE! |  | - | #VALUE! |  | )
[23 empty] | -> | #VALUE! |  | % evap
Flowrate of Condensate
|  |  |  | mL | = | mi | - | mV | = | 1000 |  | - | #VALUE! | [9 empty] | = | #VALUE! |  | kg/h
NTES | [26 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1
B
A

## BTK
| Technical Material : | [18 empty] | Doc. No. |  |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [19 empty] | Date |  |  | 2018. 3. 10.
[20 empty] | Rev. |  |  | 0
[20 empty] | Sheet No. |  |  |  | 10 | of | 12
|  | 5. | Blowdown Tank
Schematic Diagram
Vent Steam
[12 empty] | 0 |  | #VALUE!
[12 empty] | #VALUE! |  | #VALUE!
[12 empty] | mV |  | hV
|  |  |  | Blowdown Water | [7 empty] | Cooling Water | [8 empty] | Legend
|  |  |  | 20 |  | #VALUE! | [5 empty] | 3 |  | 32 | [6 empty] | P | T
|  |  |  | 1000 |  | #VALUE! | [5 empty] | #VALUE! |  | #VALUE! | [6 empty] | m | h
|  |  |  | mi |  | hi | [5 empty] | mc |  | hc | [6 empty] | P | Pressure |  |  | bar.g |  |  | bar.g |  | < Press. Unit |  | 대기압
[21 empty] | T | Temperature |  |  | ℃ |  |  | Gauge |  | < Gauge or Absolute |  | 0
[7 empty] | OP |  |  |  |  | Drain | [8 empty] | m | Flowrate |  |  | kg/h |  |  |  |  | < Temp.
[7 empty] | 0 | bar.g |  |  |  | 0 |  | 60 | [6 empty] | h | Enthalpy |  |  | kcal/kg
[12 empty] | #VALUE! |  | #VALUE! | [13 empty] | H&M Balance
[12 empty] | md |  | hd | [13 empty] | m | 1000 |  | #VALUE! | #VALUE! | #VALUE!
|  |  | T - h Diagram | [25 empty] | hi |  | hc | hV | hd
[28 empty] | h | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | Dev.
|  |  | T |  | Temp. |  | ℃ | [20 empty] | mxh | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | %
|  | #VALUE! | [16 empty] | Pressure
[19 empty] | 20 | bar.g
|  | #VALUE! | [16 empty] | Pressure
[19 empty] | 0 | bar.g
h
[6 empty] | hL |  |  |  | hi |  |  |  |  | hV | [6 empty] | Enthalpy
[6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! | [6 empty] | kcal/kg
Formulation and Calculation
|  |  |  | Steam Quality |  |  |  | * | A | -> | B
|  |  |  | x | = | ( | hi | - | hL | ) | = | ( | #VALUE! |  | - | #VALUE! |  | ) |  |  |  |  | = | #VALUE!
[6 empty] | ( | hV | - | hL | ) |  | ( | #VALUE! |  | - | #VALUE! |  | )
Flowrate of Vent Steam
|  |  |  | mV | = | mi | x | x | = | 1000 |  | x | #VALUE! | [9 empty] | = | #VALUE! |  | kg/h
Flowrate of Condensate
|  |  |  | mcd | = | mi | - | mV | = | 1000 |  | - | #VALUE! | [9 empty] | = | #VALUE! |  | kg/h
Flowrate of Cooling Water
|  |  |  | mcd |  | + | mc |  | = | md | [9 empty] | <- | Mass Conservation Law
|  |  |  | mcd | hL | + | mc | hc | = | md | hd | = | ( | mcd | + | mc | ) | hd |  | <- | Energy Conservation Law
|  |  |  | mc | = | mcd | ( | hL | - | hd | ) | = | #VALUE! |  | ( | #VALUE! |  | - | #VALUE! |  | ) |  | = | #VALUE! |  | kg/h
[7 empty] | ( | hd | - | hc | ) |  |  |  | ( | #VALUE! |  | - | #VALUE! |  | )
Flowrate of Drain
|  |  |  | md | = | mi | - | mV | + | mc | = | 1000 |  | - | #VALUE! |  | + | #VALUE! |  |  |  |  | = | #VALUE! |  | kg/h
NTES | [26 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1
B
A

## DSH
| Technical Material : | [17 empty] | Doc. No. |  |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [18 empty] | Date |  |  | 2018. 3. 10.
[19 empty] | Rev. |  |  | 0
[19 empty] | Sheet No. |  |  |  | 11 | of | 12
|  | 6. | De-superheater
Schematic Diagram
|  |  |  | Superheated Steam | [8 empty] | De-superheated Steam | [6 empty] | Legend
|  |  |  | 20 |  | 300 | [6 empty] | 19.5 |  | 250 |  |  |  |  | P | T
|  |  |  | mis |  | his | [6 empty] | mos |  | hos |  |  |  |  | m | h
[20 empty] | P | Pressure |  |  | bar.g |  |  | bar.g |  | < Press. Unit |  | 대기압
[20 empty] | T | Temperature |  |  | ℃ |  |  | Gauge |  | < Gauge or Absolute |  | 0
[20 empty] | m | Flowrate |  |  | kg/h |  |  |  |  | < Temp.
[10 empty] | Feedwater | [9 empty] | h | Enthalpy |  |  | kcal/kg
[10 empty] | 25 |  | 120
[10 empty] | mw |  | hw
|  |  |  | Superheated Steam | [5 empty] | Feedwater | [5 empty] | De-superheated Steam | [10 empty] | H&M Balance
|  |  |  | Flowrate |  | Press. |  | Temp. |  | Flowrate |  | Press. |  | Temp. |  | Flowrate | Press. |  | Temp. | [7 empty] | m | 20000 |  | #VALUE! | #VALUE!
|  |  |  | kg/h |  | bar.g |  | ℃ |  | kg/h |  | bar.g |  | ℃ |  | kg/h | bar.g |  | ℃ | [8 empty] | his |  | hw | hos
[22 empty] | ΔPdsh |  |  |  |  | h | #VALUE! |  | #VALUE! | #VALUE! | Dev.
|  |  |  | 20000 |  | 20 |  | 300 |  | #VALUE! |  | 25 |  | 120 |  | #VALUE! | 19.5 |  | 250 |  |  | 0.5 |  |  |  |  | mxh | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | %
Formulation
|  |  |  | mis |  | + | mw |  | = | mos |  |  | <- | Mass Conservation Law
|  |  |  | mis | his | + | mw | hw | = | mos | hos |  | <- | Energy Conservation Law
Case 1 : mis is given.
|  |  |  | mos | = | mis | + | mw | [13 empty] | = | #VALUE! |  | kg/h
|  |  |  | mis | his | + | mw | hw | = | mis | hos | + | mw | hos
|  |  | -> | mw | = | mis | ( | his | - | hos | ) | = | 20000 |  | ( | #VALUE! | - | #VALUE! |  | ) |  | = | #VALUE! |  | kg/h
[7 empty] | ( | hos | - | hw | ) |  |  |  | ( | #VALUE! | - | #VALUE! |  | )
Case 2 : mos is given.
|  |  |  | mis | = | mos | - | mw | [13 empty] | = | #VALUE! |  | kg/h
|  |  |  | mos | his | - | mw | his | + | mw | hw | = | mos | hos
|  |  | -> | mw | = | mos | ( | his | - | hos | ) | = | #VALUE! |  | ( | #VALUE! | - | #VALUE! |  | ) |  | = | #VALUE! |  | kg/h
[7 empty] | ( | his | - | hw | ) |  |  |  | ( | #VALUE! | - | #VALUE! |  | )
NTES | [25 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1

## SPR
| Technical Material : | [13 empty] | Doc. No. |  |  | TM - PCSC - 100
Process Calculations in Steam Cycle | [14 empty] | Date |  |  | 2018. 3. 10.
[15 empty] | Rev. |  |  | 0
[15 empty] | Sheet No. |  |  |  | 12 | of | 12
|  | 7. | Steam Pressure Reducing
|  |  | T | [10 empty] | HP Steam
|  |  | Temp. |  | ℃ | [8 empty] | 20 |  | bar.g
[14 empty] | 300 |  | ℃
[14 empty] | #VALUE! |  | m3/kg
#VALUE!
LP Steam
[14 empty] | 1 |  | bar.g
[13 empty] | TB | #VALUE! |  | ℃
[14 empty] | #VALUE! |  | kcal/kg
[14 empty] | #VALUE! |  | m3/kg
#VALUE!
[8 empty] | TD | #VALUE! |  | ℃
[9 empty] | #VALUE! |  | kcal/kg
[9 empty] | #VALUE! |  | m3/kg
h
[8 empty] | hV |  |  |  | hs |  |  |  | Enthalpy |  | kcal/kg
[8 empty] | #VALUE! |  |  |  | #VALUE!
Formulation and Calculation
Process : A -> B
Temperaure of LP Steam
|  |  |  | TB | = | Backward Equation, T( p, h ) | * | p | = | 1 | h | = | #VALUE! |  |  | = | #VALUE! |  |  | ℃
Process : C -> D
Temperaure of LP Steam
|  |  |  | TD | = | Backward Equation, T( p, h ) | * | p | = | 1 | h | = | #VALUE! |  |  | = | #VALUE! |  |  | ℃
|  |  | * | Adiabatic condition is assumed in above.
NTES | [21 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1
C
A
B
D

## form
| Technical Material : |  |  |  | Doc. No. | TM - PCSC - 100
Process Calculations in Steam Cycle |  |  |  |  | Date | 2018. 3. 10.
[5 empty] | Rev. | 0
[5 empty] | Sheet No. |  | x | of | 12
|  | x. | Aaaaaa
|  |  | x.1 | Aaaaaa
NTES | [9 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1

## 0
| Technical Material : |  |  | Doc. No. | TM - PCSC - 100
Process Calculations in Steam Cycle |  |  |  | Date | 2011. 1. 5.
|  |  |  | Rev. | 0
|  |  |  | Sheet No. |  | 0 | of | 12
|  | 0. | Aaaaaa
NTES | [8 empty] | Narai Thermal Engineering Services
Note on AD4: Cell is filled !
1