## Water Tube boiler
W A T E R & S T E A M Q U A L I T Y S T A N D A R D
1
2 | [13 empty] | Doc. No. |  | STD - WSQ - 100
3 | [13 empty] | Date |  | 2015. 6. 3.
4 | Standard |  |  | ABMA ( American Boiler Manufacturers Association ) | [9 empty] | Revision |  | 0
5 | Service |  |  | Water Tube Boiler
6
7 | [13 empty] | Sheet No. |  | 1 | of |  | 1
8 | F E E D W A T E R L I M I T
9 | Oper. Press. |  | pH |  | Dissolved Oxygen |  |  | Total Iron |  | Total Copper |  |  | Total Hardness |  | Nonvolatile TOC |  |  | Oily Matter
10 | psi.g | bar.g | --- |  | ppm |  |  | ppm |  | ppm |  |  | ppm |  | ppm |  |  | ppm
11 | 300 | #VALUE! | 8.3 | 10 | 0.007 |  |  | 0.1 |  | 0.05 |  |  | 0.3 |  | 1 |  |  | 1
12 | 450 | #VALUE! | 8.3 | 10 | 0.007 |  |  | 0.05 |  | 0.025 |  |  | 0.3 |  | 1 |  |  | 1
13 | 600 | #VALUE! | 8.3 | 10 | 0.007 |  |  | 0.03 |  | 0.02 |  |  | 0.2 |  | 0.5 |  |  | 0.5
14 | 750 | #VALUE! | 8.3 | 10 | 0.007 |  |  | 0.025 |  | 0.02 |  |  | 0.2 |  | 0.5 |  |  | 0.5
15 | 900 | #VALUE! | 8.3 | 10 | 0.007 |  |  | 0.02 |  | 0.015 |  |  | 0.1 |  | 0.5 |  |  | 0.5
16 | 1000 | #VALUE! | 8.8 | 9.6 | 0.007 |  |  | 0.02 |  | 0.01 |  |  | 0.05 |  | 0.2 |  |  | 0.2
17 | 1500 | #VALUE! | 8.8 | 9.6 | 0.007 |  |  | 0.01 |  | 0.01 |  |  | 0.05 |  | 0.2 |  |  | 0.2
18 | 2000 | #VALUE! | 8.8 | 9.6 | 0.007 |  |  | 0.01 |  | 0.01 |  |  | 0.05 |  | 0.2 |  |  | 0.2
19 | B O I L E R W A T E R L I M I T
20 | Oper. Press. |  | TDS |  | Total Alkalinity as CaCO3 |  |  |  | Suspended Solids |  |  | Silica as SiO2 *1) |  | PO43- *2)
21 | psi.g | bar.g | ppm |  | ppm |  |  |  | ppm |  |  | ppm |  | ppm
22 | 300 | #VALUE! | 3500 |  | 700 |  |  |  | 15 |  |  | 150 |  | 20 | 40
23 | 450 | #VALUE! | 3000 |  | 600 |  |  |  | 10 |  |  | 90 |  | 20 | 40
24 | 600 | #VALUE! | 2500 |  | 500 |  |  |  | 8 |  |  | 40 |  | 20 | 40
25 | 750 | #VALUE! | 1000 |  | 200 |  |  |  | 3 |  |  | 30 |  | 20 | 40
26 | 900 | #VALUE! | 750 |  | 150 |  |  |  | 2 |  |  | 20 |  | 5 | 15
27 | 1000 | #VALUE! | 625 |  | 125 |  |  |  | 1 |  |  | 8 |  | 5 | 15
28 | 1800 | #VALUE! | 100 |  | - N/A - |  |  |  | 1 |  |  | 2 |  | 3 | 5
29 | 2350 | #VALUE! | 50 |  | - N/A - |  |  |  | 1 |  |  | 1
30 | 2600 | #VALUE! | 25 |  | - N/A - |  |  |  | 1 |  |  | 0.5
31 | 2900 | #VALUE! | 15 |  | - N/A - |  |  |  | 1 |  |  | 0.5
32 |  |  |  |  | * | 20 | % of TDS
33 | S T E A M L I M I T
34 | Oper. Press. |  | TDS *3)
35 | psi.g | bar.g | ppm
36 | 300 | #VALUE! | 1
37 | 450 | #VALUE! | 1
38 | 600 | #VALUE! | 1
39 | 750 | #VALUE! | 0.5
40 | 900 | #VALUE! | 0.5
41 | 1000 | #VALUE! | 0.5
42 | 1800 | #VALUE! | 0.1
43 | 2350 | #VALUE! | 0.1
44 | 2600 | #VALUE! | 0.05
45 | 2900 | #VALUE! | 0.05
46 | - B L A N K -
47
48
49
50
51
52
53 | Notes
54 | *1) | from ASME.
55 | *2) | from JBMA.
56 | *3) | The value is that corresponding to max. BW TDS. | [7 empty] | The actual value is directly proportional to the actual value of BW TDS.
57 | *4) | Total Dissoved Solid ( TDS ) in ppm | [5 empty] | = | 0.7 | x | Conductivity in μS/cm
58 | *5)
59 | *6)
60 | *7)
| NTES | [17 empty] | Narai Thermal Engineering Services

## Data Sheet
W A T E R & S T E A M Q U A L I T Y D A T A S H E E T
1 | Project |  |  | P | [10 empty] | Job No. |  | JN |  |  |  | Job No.
2 | Client |  |  | C | [10 empty] | Doc. No. |  | DS - WSQ - 100
3 | Contractor |  |  | CC | [10 empty] | Date |  | 2015. 6. 3.
4 | Standard |  |  | ABMA ( American Boiler Manufacturers Association ) | [10 empty] | Revision |  | 0
5 | Service of Unit |  |  | Water Tube Boiler | [10 empty] | Item No. |  | B - 100
6
7 | [14 empty] | Sheet No. |  | 1 | of |  | 1
8 | B O I L E R D E S I G N D A T A
9 | Operating |  | Pressure |  |  | 45 |  | bar.g
10 |  |  | Temperature |  |  | #VALUE! |  | ℃
11
12 | Q U A L I T Y f o r F E E D W A T E R | [19 empty] | #VALUE! | psi.g | F E E D W A T E R
13 | [5 empty] | Recommendation |  |  |  | Project Data | [10 empty] | psi.g | bar.g | pH |  | Dissolved Oxygen | Total Iron | Total Copper | Total Hardness | Nonvolatile TOC | Oily Matter
14 | pH |  | @ 25 ℃ |  |  | #VALUE! | ~ | #VALUE! |  | #VALUE! | ~ | #VALUE! | [8 empty] | 300 | #VALUE! | 8.3 | 10 | 0.007 | 0.1 | 0.05 | 0.3 | 1 | 1
15 | Conductivity |  | @ 25 ℃ |  | max. |  |  |  |  | 10 |  |  | μS/cm | [7 empty] | 450 | #VALUE! | 8.3 | 10 | 0.007 | 0.05 | 0.025 | 0.3 | 1 | 1
16 | TDS |  |  |  | max. |  |  |  |  | 7 |  |  | ppm | [7 empty] | 600 | #VALUE! | 8.3 | 10 | 0.007 | 0.03 | 0.02 | 0.2 | 0.5 | 0.5
17 | Dissolved Oxygen |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | ppm | [7 empty] | 750 | #VALUE! | 8.3 | 10 | 0.007 | 0.025 | 0.02 | 0.2 | 0.5 | 0.5
18 | Total Iron |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | ppm | [7 empty] | 900 | #VALUE! | 8.3 | 10 | 0.007 | 0.02 | 0.015 | 0.1 | 0.5 | 0.5
19 | Total Copper |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | ppm | [7 empty] | 1000 | #VALUE! | 8.8 | 9.6 | 0.007 | 0.02 | 0.01 | 0.05 | 0.2 | 0.2
20 | Total Hardness |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | ppm | [7 empty] | 1500 | #VALUE! | 8.8 | 9.6 | 0.007 | 0.01 | 0.01 | 0.05 | 0.2 | 0.2
21 | Nonvolatile TOC |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | ppm | [7 empty] | 2000 | #VALUE! | 8.8 | 9.6 | 0.007 | 0.01 | 0.01 | 0.05 | 0.2 | 0.2
22 | Oily Matter |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | ppm
23
24 | Q U A L I T Y f o r B O I L E R W A T E R | [19 empty] | #VALUE! | psi.g | B O I L E R W A T E R
25 | [5 empty] | Recommendation |  |  |  | Operating Value | [10 empty] | psi.g | bar.g | TDS | Total Alkalinity, CaCO3 | Suspended Solids | Silica as SiO2 | PO43-
26 | TDS |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | ppm | [7 empty] | 300 | #VALUE! | 3500 | 700 | 15 | 150 | 20 | 40
27 |  |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | μS/cm | [7 empty] | 450 | #VALUE! | 3000 | 600 | 10 | 90 | 20 | 40
28 | Total Alkalinity, CaCO3 |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | ppm | [7 empty] | 600 | #VALUE! | 2500 | 500 | 8 | 40 | 20 | 40
29 | Suspended Solids |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | ppm | [7 empty] | 750 | #VALUE! | 1000 | 200 | 3 | 30 | 20 | 40
30 | Silica as SiO2 |  |  |  | max. | #VALUE! |  |  | *1) | #VALUE! |  |  | ppm | [7 empty] | 900 | #VALUE! | 750 | 150 | 2 | 20 | 5 | 15
31 | PO43- |  |  |  |  | #VALUE! | ~ | #VALUE! | *2) | #VALUE! | ~ | #VALUE! | ppm | [7 empty] | 1000 | #VALUE! | 625 | 125 | 1 | 8 | 5 | 15
32 | [20 empty] | 1800 | #VALUE! | 100 | - N/A - | 1 | 2 | 3 | 5
33 | Q U A L I T Y f o r S T E A M | [19 empty] | 2350 | #VALUE! | 50 | - N/A - | 1 | 1
34 | [5 empty] | Expected Value |  |  |  | Guaranteed Value | [10 empty] | 2600 | #VALUE! | 25 | - N/A - | 1 | 0.5
35 | TDS |  |  |  | max. | #VALUE! |  |  | *3) | #VALUE! |  |  | ppm | [7 empty] | 2900 | #VALUE! | 15 | - N/A - | 1 | 0.5
36 |  |  |  |  | max. | #VALUE! |  |  |  | #VALUE! |  |  | μS/cm | [10 empty] | 20 | % of TDS
37 | Quality, Dryness |  |  |  | max. |  |  |  |  | 99.5 |  |  | % | [7 empty] | #VALUE! | psi.g | S T E A M
38 | Silica |  |  |  | max. |  |  |  |  | 0.2 |  |  | ppm | [7 empty] | psi.g | bar.g | TDS
39 | [20 empty] | 300 | #VALUE! | 1
40 | [20 empty] | 450 | #VALUE! | 1
41 | - B L A N K - | [19 empty] | 600 | #VALUE! | 1
42 | [20 empty] | 750 | #VALUE! | 0.5
43 | [20 empty] | 900 | #VALUE! | 0.5
44 | [20 empty] | 1000 | #VALUE! | 0.5
45 | [20 empty] | 1800 | #VALUE! | 0.1
46 | [20 empty] | 2350 | #VALUE! | 0.1
47 | [20 empty] | 2600 | #VALUE! | 0.05
48 | [20 empty] | 2900 | #VALUE! | 0.05
49
50 | Notes
51 | *1) | from ASME.
52 | *2) | from JBMA.
53 | *3) | The value is that corresponding to max. BW TDS. | [7 empty] | The actual value is directly proportional to the actual value of BW TDS.
54 | *4) | Max. Allowable TDS in Feedwater, Fmax
55 |  | Fmax | = | ( B x Rd + S x 100 ) / ( Rd + 100 ) |  |  |  |  | = | #VALUE! |  | ppm | -> | Divided by |  | 0.7 | = | #VALUE! | μS/cm |  | Calculation of Blowdown Rate, R for Operation
56 |  |  | Where, |  | TDS | Boiler Water |  |  | B | #VALUE! |  | ppm |  | Steam | S | #VALUE! |  | ppm |  |  | R | = | ( F - S ) / ( B - F ) x 100 |  |  |  |  | = | #VALUE! |  | % | Max.
57 |  |  |  |  | Design Blowdown Rate |  |  |  | Rd | 3 |  | % | [9 empty] | Where, |  | TDS | Feedwater |  |  | F | 20 |  | ppm | #VALUE!
58 | *5) | [23 empty] | Boiler Water |  |  | B | 2000 |  | ppm | #VALUE!
59 | *6) | [23 empty] | Steam |  |  | S | #VALUE! |  | ppm
60 | *7)
| NTES | [18 empty] | Narai Thermal Engineering Services

## F&S Tube Boiler
W A T E R & S T E A M Q U A L I T Y S T A N D A R D
1
2 | [11 empty] | Doc. No. |  | STD - WSQ - 200
3 | [11 empty] | Date |  | 2015. 1. 10.
4 | Standard |  |  | ABMA ( American Boiler Manufacturers Association ) | [7 empty] | Revision |  | 0
5 | Service |  |  | Fire & Smoke Tube Boiler
6
7 | [11 empty] | Sheet No. |  | 1 | of |  | 1
8 | F E E D W A T E R L I M I T
9 | Oper. Press. |  | pH |  | Dissolved Oxygen | Total Iron |  | Total Copper |  |  | Total Hardness |  | Nonvolatile TOC |  |  | Oily Matter
10 | psi.g | bar.g | --- |  | ppm | ppm |  | ppm |  |  | ppm |  | ppm |  |  | ppm
11 | 15 | #VALUE! | 8.3 | 10.5 | 0.03 | 0.1 |  | 0.05 |  |  | 1 |  | 10 |  |  | 1
12 | 300 | #VALUE! | 8.3 | 10.5 | 0.007 | 0.1 |  | 0.05 |  |  | 1 |  | 10 |  |  | 1
13
14
15
16
17
18
19 | B O I L E R W A T E R L I M I T
20 | Oper. Press. |  | TDS |  | Total Alkalinity as CaCO3 |  | Suspended Solids |  |  | Silica as SiO2 |  | Total Iron
21 | psi.g | bar.g | ppm |  | ppm |  | ppm |  |  | ppm |  | ppm
22 | 15 | #VALUE! | 5000 |  | 1200 |  | 100 |  |  | 150 |  | 10
23 | 250 | #VALUE! | 5000 |  | 1200 |  | 100 |  |  | 150 |  | 10
24 | 350 | #VALUE! | 4000 |  | 900 |  | 25 |  |  | 120 |  | 8
25 | 500 | #VALUE! | 3000 |  | 800 |  | 10 |  |  | 80 |  | 5
26
27
28
29
30
31
32
33 | S T E A M L I M I T
34 | Oper. Press. |  | TDS *1)
35 | psi.g | bar.g | ppm
36 | 15 | #VALUE! | 2
37 | 250 | #VALUE! | 2
38 | 350 | #VALUE! | 1.5
39 | 500 | #VALUE! | 1
40
41
42
43
44
45
46 | - B L A N K -
47
48
49
50
51
52
53 | Notes
54 | *1) | The value is that corresponding to max. BW TDS. | [5 empty] | The actual value is directly proportional to the actual value of BW TDS.
55 | *2) | Total Dissoved Solid ( TDS ) in ppm |  |  |  | = | 0.7 | x | Conductivity in μS/cm
56 | *3)
57 | *4)
58 | *5)
59 | *6)
60 | *7)
| NTES | [15 empty] | Narai Thermal Engineering Services

## _Data Sheet
W A T E R & S T E A M Q U A L I T Y D A T A S H E E T
1 | Project |  |  | P | [9 empty] | Job No. |  | JN |  |  |  | Job No.
2 | Client |  |  | C | [9 empty] | Doc. No. |  | DS - WSQ - 200
3 | Contractor |  |  | CC | [9 empty] | Date |  | 2015. 1. 10.
4 | Standard |  |  | ABMA ( American Boiler Manufacturers Association ) | [9 empty] | Revision |  | 0
5 | Service of Unit |  |  | Fire & Smoke Tube Boiler | [9 empty] | Item No. |  | B - 100
6
7 | [13 empty] | Sheet No. |  | 1 | of |  | 1
8 | B O I L E R D E S I G N D A T A
9 | Operating |  | Pressure |  |  | 10 |  | bar.g
10 |  |  | Temperature |  |  | #VALUE! |  | ℃
11
12 | Q U A L I T Y f o r F E E D W A T E R | [18 empty] | #VALUE! | psi.g | F E E D W A T E R
13 | pH |  |  |  |  | #VALUE! | ~ | #VALUE! | [11 empty] | psi.g | bar.g | pH |  | Dissolved Oxygen | Total Iron | Total Copper | Total Hardness | Nonvolatile TOC | Oily Matter
14 | Dissolved Oxygen |  |  |  | max. | #VALUE! |  |  | ppm | [10 empty] | 15 | #VALUE! | 8.3 | 10.5 | 0.03 | 0.1 | 0.05 | 1 | 10 | 1
15 | Total Iron |  |  |  | max. | #VALUE! |  |  | ppm | [10 empty] | 300 | #VALUE! | 8.3 | 10.5 | 0.007 | 0.1 | 0.05 | 1 | 10 | 1
16 | Total Copper |  |  |  | max. | #VALUE! |  |  | ppm
17 | Total Hardness |  |  |  | max. | #VALUE! |  |  | ppm
18 | Nonvolatile TOC |  |  |  | max. | #VALUE! |  |  | ppm
19 | Oily Matter |  |  |  | max. | #VALUE! |  |  | ppm
20
21 | Q U A L I T Y f o r B O I L E R W A T E R | [18 empty] | #VALUE! | psi.g | B O I L E R W A T E R
22 | TDS |  |  |  | max. | #VALUE! |  |  | ppm | [10 empty] | psi.g | bar.g | TDS | Total Alkalinity, CaCO3 | Suspended Solids | Silica as SiO2 | Total Iron
23 | Total Alkalinity, CaCO3 |  |  |  | max. | #VALUE! |  |  | ppm | [10 empty] | 15 | #VALUE! | 5000 | 1200 | 100 | 150 | 10
24 | Suspended Solids |  |  |  | max. | #VALUE! |  |  | ppm | [10 empty] | 250 | #VALUE! | 5000 | 1200 | 100 | 150 | 10
25 | Silica as SiO2 |  |  |  | max. | #VALUE! |  |  | ppm | [10 empty] | 350 | #VALUE! | 4000 | 900 | 25 | 120 | 8
26 | Total Iron |  |  |  | max. | #VALUE! |  |  | ppm | [10 empty] | 500 | #VALUE! | 3000 | 800 | 10 | 80 | 5
27
28
29 | Q U A L I T Y f o r S T E A M | [18 empty] | #VALUE! | psi.g | S T E A M
30 | TDS |  |  |  | max. | #VALUE! |  |  | ppm | *1) | [9 empty] | psi.g | bar.g | TDS
31 | Quality, Dryness |  |  |  | max. | 99.5 |  |  | % | [10 empty] | 15 | #VALUE! | 2
32 | Silica |  |  |  | max. | 0.2 |  |  | ppm | [10 empty] | 250 | #VALUE! | 2
33 | [19 empty] | 350 | #VALUE! | 1.5
34 | [19 empty] | 500 | #VALUE! | 1
35 | - B L A N K -
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50 | Notes
51 | *1) | The value is that corresponding to max. BW TDS. | [7 empty] | The actual value is directly proportional to the actual value of BW TDS.
52 | *2) | Max. Allowable TDS in Feedwater, Fmax
53 |  | Fmax | = | ( B x Rd + S x 100 ) / ( Rd + 100 ) |  |  |  |  | = | #VALUE! | ppm | -> | Divided by |  | 0.7 | = | #VALUE! | μS/cm
54 |  |  | Where, |  | TDS | Boiler Water |  |  | B | #VALUE! | ppm |  | Steam | S | #VALUE! |  | ppm |  |  | Calculation of Blowdown Rate, R for Operation
55 |  |  |  |  | Design Blowdown Rate |  |  |  | Rd | 3 | % Steam Flow | [8 empty] | R | = | ( F - S ) / ( B - F ) x 100 |  |  |  |  | = | #VALUE! |  | % | Max.
56 | *3) | [19 empty] | Where, |  | TDS | Feedwater |  |  | F | 20 |  | ppm | #VALUE!
57 | *4) | [22 empty] | Boiler Water |  |  | B | 2000 |  | ppm | #VALUE!
58 | *5) | [22 empty] | Steam |  |  | S | #VALUE! |  | ppm
59 | *6)
60 | *7)
| NTES | [17 empty] | Narai Thermal Engineering Services

## a
D E S I G N I N F O R M A T I O N
1 | Project | #NAME? | Job No. | #NAME?
2 | Client | #NAME? | Doc. No. | DI - AAA - 100
3 | Contractor | #NAME? | Date | 2008. 8. 1.
4 | Code/Standard | #NAME? | Revision | 0
5 | Service of Unit | #NAME? | Item No. | #NAME?
6 | Type | #NAME?
7
8 | A A A A A
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26 | B B B B B
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47 | - B L A N K -
48
49
50
51
52
53
54
55 | Notes
56 | *1)
57 | *2)
58 | *3)
59 | *4)
60 | *5)
| #NAME? |  |  |  | #NAME?